## Print - Specs
SECTION 16990A
CONDUIT SCHEDULE
AREA 01
PART 1 GENERAL
1.01 SUMMARY
| A. |  | Conduit requirements:
1. As defined in Section 16050 and Section 16130.
| B. |  | Cable requirements and definitions:
1. As defined in Section 16050 and Section 16123.
|  |  | 2. 3/CS#16: |  |  |  | 3 conductor, 16 gauge, twisted shielded triplet.
|  |  | 3. */C#Y: |  |  |  | Multiconductor cable (* indicates number of
conductors, Y indicates conductor size and insulation).
|  |  | 4. */FO: |  |  |  | Fiber optic (* indicates strand count).
|  |  | 5. CAT6: |  |  |  | Category 6 Ethernet cable.
|  |  | 6. PULL: |  |  |  | Pull Rope.
PART 2 PRODUCTS
Not Used.
PART 3 EXECUTION
3.01 CONDUIT SCHEDULE
| A. |  | Conduit Schedule is presented on the following pages.
CONDUIT SCHEDULE AREA 01 | [12 empty] | ENGINEER | SKB
JORDAN VALLEY WATER TREATMENT PLANT | [12 empty] | REVISION | 0
SITE | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-01-091 | 02E03 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-01-501 | 01E02 | 2 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | CL2-ALARM STROBE |  |  |  | C-01-502
| 02E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | CL2-ALARM STROBE CONTROL | 0
C-01-502 | 02E01 | 2 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PB-15 |  |  |  | C-01-503
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | CL2-ALARM STROBE CONTROL | C-01-501
C-01-503 | 02E01 | 2 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PB-14 |  |  |  | C-01-504
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | CL2-ALARM STROBE CONTROL | C-01-502
C-01-504 | 02E01 | 2 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PB-13
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | CLIP PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | CL2-ALARM STROBE CONTROL | C-01-503
C-01-601 | 01E03 | 1 | 3 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6001 |  |  |  | C-01-602
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #2A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6001 CONTROL | 0
C-01-602 | 01E03 | 1 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6002 |  |  |  | C-01-603
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #3A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6001 CONTROL | C-01-601
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6002 CONTROL | 0
C-01-603 | 01E03 | 1 | 9 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6003 |  |  |  | C-01-604
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #4A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6001 CONTROL | C-01-602
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6002 CONTROL | C-01-602
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6003 CONTROL | 0
C-01-604 | 01E03 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6004 |  |  |  | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #5A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6001 CONTROL | C-01-603
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6002 CONTROL | C-01-603
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6003 CONTROL | C-01-603
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6004 CONTROL | 0
C-01-605 | 01E03 | 2 | 33 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6005 |  |  |  | C-01-615
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6001 CONTROL | C-01-604
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6002 CONTROL | C-01-604
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6003 CONTROL | C-01-604
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6004 CONTROL | C-01-604
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6005 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6006 CONTROL | C-01-606
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6007 CONTROL | C-01-606
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6008 CONTROL | C-01-606
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6009 CONTROL | C-01-609
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6010 CONTROL | C-01-609
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6011 CONTROL | C-01-609
C-01-606 | 01E03 | 1 | 9 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6006 |  |  |  | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #5A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6006 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6007 CONTROL | C-01-607
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6008 CONTROL | C-01-607
C-01-607 | 01E03 | 1 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6007 |  |  |  | C-01-606
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #6A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6007 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6008 CONTROL | C-01-608
C-01-608 | 01E03 | 1 | 3 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6008 |  |  |  | C-01-607
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #7A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6008 CONTROL | 0
C-01-609 | 01E03 | 1 | 9 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6009 |  |  |  | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #5A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6009 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6010 CONTROL | C-01-610
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6011 CONTROL | C-01-610
C-01-610 | 01E03 | 1 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6010 |  |  |  | C-01-609
| 01E04 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #9A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6010 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6011 CONTROL | C-01-611
C-01-611 | 01E04 | 1 | 3 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6011 |  |  |  | C-01-610
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #10A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6011 CONTROL | 0
CONDUIT SCHEDULE AREA 01 | [12 empty] | ENGINEER | SKB
JORDAN VALLEY WATER TREATMENT PLANT | [12 empty] | REVISION | 0
SITE | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-01-615 | 02E01 | 2 | 33 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PB-13
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6001 CONTROL | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6002 CONTROL | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6003 CONTROL | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6004 CONTROL | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6005 CONTROL | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6006 CONTROL | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6007 CONTROL | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6008 CONTROL | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6009 CONTROL | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6010 CONTROL | C-01-605
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | LSH-6011 CONTROL | C-01-605
L-01-042 | 01E02 | 2 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | POLE LIGHT |  |  |  | L-01-043
| 02E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | POLE LIGHT POWER | 0
L-01-043 | 02E03 | 2 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PB-15 |  |  |  | L-01-503
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-18
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | POLE LIGHT POWER | L-01-042
L-01-051 | 01E02 | 2 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | BACKWASH TANK LVL HEATER |  |  |  | L-01-502
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | BACKWASH TANK LVL HEATER POWER | 0
L-01-061 | 01E02 | 2 | 2 | #8 | XHHW-2 | 1 | #8 | XHHW-2 | FR: | ELECTRONICS ENCLOSURE |  |  |  | L-01-062
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-18
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #8 | >> | ELECTRONICS ENCLOSURE POWER | 0
L-01-062 | 02E03 | 2 | 2 | #8 | XHHW-2 | 1 | #8 | XHHW-2 | FR: | PB-18 |  |  |  | L-01-063
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #8 | >> | ELECTRONICS ENCLOSURE POWER | L-01-061
L-01-063 | 02E01 | 2 | 2 | #8 | XHHW-2 | 1 | #8 | XHHW-2 | FR: | PB-15 |  |  |  | L-01-064
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #8 | >> | ELECTRONICS ENCLOSURE POWER | L-01-062
L-01-064 | 02E01 | 2 | 2 | #8 | XHHW-2 | 1 | #8 | XHHW-2 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #8 | >> | ELECTRONICS ENCLOSURE POWER | L-01-063
L-01-185 | 02E02 | 2 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | PMP-6852
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
| 68E03 |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | PMP-6852 POWER | 0
L-01-501 | 01E02 | 2 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | SOUTH SECURITY GATE |  |  |  | L-01-502
| 02E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | SOUTH SECURITY GATE POWER | 0
L-01-502 | 02E03 | 2 | 4 | #10 | XHHW-2 | 1 | #6 | XHHW-2 | FR: | PB-15 |  |  |  | L-01-503
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-18
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | BACKWASH TANK LVL HEATER POWER | L-01-051
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | SOUTH SECURITY GATE POWER | L-01-501
L-01-503 | 01E02 | 2 | 4 | #10 | XHHW-2 | 1 | #6 | XHHW-2 | FR: | PB-18
|  |  | 4 | #12 | XHHW-2 |  |  | 0 | TO: | PNL-CELL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | POLE LIGHT POWER | L-01-043
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | BACKWASH TANK LVL HEATER POWER | L-01-502
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | SOUTH SECURITY GATE POWER | L-01-502
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | S SECURITY GATE CAMERA POWER | L-01-542
L-01-521 | 01E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | XFMR-RES
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CELL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | XFMR-RES POWER | 0
L-01-522 | 01E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | ELECTRONICS ENCLOSURE
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CELL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | ELECTRONICS ENCLOSURE POWER | 0
L-01-531 | 01E02 | 1.5 | 3 | #1/0 | XHHW-2 | 1 | #6 | XHHW-2 | FR: | PNL-CELL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-CELL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #1/0 | >> | PNL-CELL POWER | 0
L-01-541 | 01E02 | 2 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | S SECURITY GATE CAMERA |  |  |  | L-01-542
| 02E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | S SECURITY GATE CAMERA POWER | 0
L-01-542 | 02E03 | 2 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PB-15 |  |  |  | L-01-503
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-18
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | S SECURITY GATE CAMERA POWER | L-01-541
CONDUIT SCHEDULE AREA 01 | [12 empty] | ENGINEER | SKB
JORDAN VALLEY WATER TREATMENT PLANT | [12 empty] | REVISION | 0
SITE | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
M-01-001 | 02E03 | 4 | 1 | #2/0:15KV | 15KV-EPR | 1 | #2/0 | XHHW-2 | FR: | XFMR CELL |  |  |  | M-01-002
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-17
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | #2/0:15KV | >> | XFMR CELL POWER | 0
M-01-002 | 02E03 | 4 | 1 | #2/0:15KV | 15KV-EPR | 1 | #4 | XHHW-2 | FR: | PB-17
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECTIONALIZER 2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | #2/0:15KV | >> | XFMR CELL POWER | M-01-001
N-01-501 | 01E02 | 2 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | S SECURITY GATE CAMERA |  |  |  | N-01-503
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | WEST GATE OPERATOR
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | S SECURITY GATE CAMERA NETWORK | 0
N-01-502 | 01E02 | 2 | 4 | 2/C-#14 | 0 | 1 | #14 | XHHW-2 | FR: | CALLBOX |  |  |  | N-01-503
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | WEST GATE OPERATOR
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/C-#14 | >> | CALLBOX NETWORK (TEMP) | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/C-#14 | >> | CALLBOX NETWORK (PERMANENT) | 0
N-01-503 | 02E03 | 2 | 4 | 2/C-#14 | 0 | 1 | #14 | XHHW-2 | FR: | WEST GATE OPERATOR |  |  |  | N-01-504
|  |  | 1 | 0 | CAT6 |  |  | 0 | TO: | PB-15
|  |  | 1 | 0 | 12/FO |  |  | 0 |  | 1 | CAT6 | >> | S SECURITY GATE CAMERA NETWORK | N-01-501
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/C-#14 | >> | CALLBOX NETWORK (TEMP) | N-01-502
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/C-#14 | >> | CALLBOX NETWORK (PERMANENT) | N-01-502
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | S SECURITY GATE NETWORK | 0
N-01-504 | 02E03 | 2 | 2 | 2/C-#14 | 0 | 1 | #14 | XHHW-2 | FR: | PB-15 |  |  |  | N-01-521
|  |  | 1 | 0 | CAT6 |  |  | 0 | TO: | PB-18
|  |  | 1 | 0 | 12/FO |  |  | 0 |  | 1 | CAT6 | >> | S SECURITY GATE CAMERA NETWORK | N-01-503
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/C-#14 | >> | CALLBOX NETWORK (TEMP) | N-01-503
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | S SECURITY GATE NETWORK | N-01-503
N-01-505 | 02E01 | 2 | 2 | 2/C-#14 | 0 | 1 | #14 | XHHW-2 | FR: | PB-15 |  |  |  | N-01-506
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/C-#14 | >> | CALLBOX NETWORK (PERMANENT) | N-01-503
N-01-506 | 02E01 | 2 | 4 | 2/C-#14 | 0 | 1 | #14 | XHHW-2 | FR: | PB-14
|  |  | 1 | 0 | CAT6 |  |  | 0 | TO: | RTU-CS
|  |  | 1 | 0 | 12/FO |  |  | 0 |  | 1 | CAT6 | >> | S SECURITY GATE CAMERA NETWORK | N-01-505
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/C-#14 | >> | CALLBOX NETWORK (TEMP) | N-01-505
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/C-#14 | >> | CALLBOX NETWORK (PERMANENT) | N-01-505
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | S SECURITY GATE NETWORK | N-01-505
N-01-511 | 01E02 | 2 | 1 | 3/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | GATE CARD READER |  |  |  | N-01-521
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-18
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 3/CS-#16 | >> | GATE CARD READER NETWORK | 0
N-01-521 | 01E02 | 2.5 | 2 | 2/C-#14 | 0 | 1 | #14 | XHHW-2 | FR: | PB-18 (INTERCEPTED FIBER OPTIC TO CULINARY RESERVOIR)
|  |  | 1 | 0 | CAT6 |  |  | 0 | TO: | ELECTRONICS ENCLOSURE
|  |  | 2 | 0 | 12/FO |  |  | 0 |  | 1 | CAT6 | >> | S SECURITY GATE CAMERA NETWORK | N-01-504
|  |  | 1 | 3/CS-#16 | 0 |  |  | 0 |  | 2 | 2/C-#14 | >> | CALLBOX NETWORK (TEMP) | N-01-504
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | S SECURITY GATE NETWORK | N-01-504
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 3/CS-#16 | >> | GATE CARD READER NETWORK | N-01-511
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | CULINARY RESERVOIR NETWORK | 0
N-01-525 | 01E02 | 2 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | ELECTRONICS ENCLOSURE |  |  |  | N-01-526
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-18
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | ELECTRONICS ENCLOSURE NETWORK | 0
N-01-526 | 02E03 | 2 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | PB-18 |  |  |  | N-01-527
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | ELECTRONICS ENCLOSURE NETWORK | N-01-525
N-01-527 | 02E01 | 2 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | PB-15 |  |  |  | N-01-528
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | ELECTRONICS ENCLOSURE NETWORK | N-01-526
N-01-528 | 02E01 | 2 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | ELECTRONICS ENCLOSURE NETWORK | N-01-527
N-01-531 | 01E02 | 2 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | ELECTRONICS ENCLOSURE |  |  |  | N-01-922
| 02E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | ELECTRONICS ENCLOSURE NETWORK | 0
N-01-611 | 02E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | WIRELESS NETWORK J-BOX
| 68E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-01-901 | 68E03 | 1.5 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | VCP-6800 |  |  |  | N-01-903
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | VCP-6800 NETWORK | 0
CONDUIT SCHEDULE AREA 01 | [12 empty] | ENGINEER | SKB
JORDAN VALLEY WATER TREATMENT PLANT | [12 empty] | REVISION | 0
SITE | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
N-01-902 | 68E03 | 1.5 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | VCP-6830 |  |  |  | N-01-903
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | VCP-6830 NETWORK | 0
N-01-903 | 02E02 | 2 | 2 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | J-BOX
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
| 68E03 |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | VCP-6800 NETWORK | N-01-901
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | VCP-6830 NETWORK | N-01-902
N-01-911 | 02E02 | 2 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | RTU-CL |  |  |  | N-01-921
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CL NETWORK | 0
N-01-912 | 02E02 | 2 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | RTU-CS |  |  |  | N-01-921
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CS NETWORK | 0
N-01-921 | 02E02 | 2 | 2 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | PB-16 |  |  |  | N-01-922
| 02E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CL NETWORK | N-01-911
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CS NETWORK | N-01-912
N-01-922 | 01E03 | 3 | 3 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | PB #2 |  |  |  | N-01-923
| 30E10 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #11 (VIA SPARE 3" CONDUIT IN EXISTING DUCT BANK)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CL NETWORK | N-01-921
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CS NETWORK | N-01-921
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | ELECTRONICS ENCLOSURE NETWORK | N-01-531
N-01-923 | 30E10 | 3 | 3 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | PB #11 |  |  |  | N-01-924
| 71E02 |  | 0 | 0 | 0 |  |  | 0 | TO: | EXISTING PULLBOX (VIA EXISTING EXPOSED 3" CONDUIT)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CL NETWORK | N-01-922
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CS NETWORK | N-01-922
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | ELECTRONICS ENCLOSURE NETWORK | N-01-922
N-01-924 | 69E01 | 3 | 3 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | EXISTING PULLBOX |  |  |  | N-01-925
| 71E02 |  | 0 | 0 | 0 |  |  | 0 | TO: | EXISTING PULLBOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CL NETWORK | N-01-923
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CS NETWORK | N-01-923
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | ELECTRONICS ENCLOSURE NETWORK | N-01-923
N-01-925 | 69E01 | 2.5 | 3 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | EXISTING PULLBOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LEVEL 2 NETWORK ROOM
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CL NETWORK | N-01-924
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-CS NETWORK | N-01-924
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | ELECTRONICS ENCLOSURE NETWORK | N-01-924
N-01-931 | 30E19 | 1.5 | 1 | PULL | ROPE | 0 |  | 0 | FR: | EXISTING PULLBOX |  |  |  | N-01-932
| 69E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | VIA CABLE TRAY
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-01-932 | 69E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | CABLE TRAY
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | CELL SITE EQUIP ROOM VIA EXISTING CONDUIT
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | N-01-931
P-01-031 | 02E01 | 2 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PB-15 (CONNECT EXISTING WIRES IN INTERCEPTED DUCTBANK) |  |  |  | P-01-032
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | RESERVOIR TANK LIGHT & HEATING | 0
P-01-032 | 02E01 | 2 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | RESERVOIR TANK LIGHT & HEATING | P-01-031
P-01-071 | 01E05 | 3 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | MCC-BL |  |  |  | P-01-072
| 30E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #7 (VIA EXISTING DUCT BANK)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | MCC-BL POWER | 0
P-01-072 | 02E03 | 4 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | PB #7
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | MCC-BL POWER | P-01-071
P-01-081 | 01E05 | 3 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | MCC-BL |  |  |  | P-01-082
| 30E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #7 (VIA EXISTING DUCT BANK)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | MCC-BL POWER | 0
P-01-082 | 02E03 | 4 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | PB #7
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | MCC-BL POWER | P-01-081
P-01-091 | 02E03 | 4 | 4 | 500 | XHHW-2 | 1 | #1/0 | XHHW-2 | FR: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | 500 | >> | SWBD-APF POWER | 0
CONDUIT SCHEDULE AREA 01 | [12 empty] | ENGINEER | SKB
JORDAN VALLEY WATER TREATMENT PLANT | [12 empty] | REVISION | 0
SITE | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-01-092 | 02E03 | 4 | 4 | 500 | XHHW-2 | 1 | #1/0 | XHHW-2 | FR: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | 500 | >> | SWBD-APF POWER | 0
P-01-093 | 02E03 | 4 | 4 | 500 | XHHW-2 | 1 | #1/0 | XHHW-2 | FR: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | 500 | >> | SWBD-APF POWER | 0
P-01-101 | 02E01 | 4 | 3 | #4/0 | XHHW-2 | 1 | #2 | XHHW-2 | FR: | MCC-CS |  |  |  | P-01-102
| 65E02 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-CS POWER | 0
P-01-102 | 02E01 | 4 | 3 | #4/0 | XHHW-2 | 1 | #2 | XHHW-2 | FR: | PB-14 |  |  |  | P-01-103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-CS POWER | P-01-101
P-01-103 | 02E01 | 4 | 3 | #4/0 | XHHW-2 | 1 | #2 | XHHW-2 | FR: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-CS POWER | P-01-102
P-01-105 | 02E01 | 4 | 3 | #4/0 | XHHW-2 | 1 | #2 | XHHW-2 | FR: | MCC-CS |  |  |  | P-01-106
| 65E02 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-CS POWER | 0
P-01-106 | 02E01 | 4 | 3 | #4/0 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | PB-14 |  |  |  | P-01-107
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-CS POWER | P-01-105
P-01-107 | 02E01 | 4 | 3 | #4/0 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-CS POWER | P-01-106
P-01-121 | 02E01 | 4 | 3 | #4/0 | XHHW-2 | 1 | #2 | XHHW-2 | FR: | MCC-CL |  |  |  | P-01-122
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-CL POWER | 0
P-01-122 | 02E01 | 4 | 3 | #4/0 | XHHW-2 | 1 | #2 | XHHW-2 | FR: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-CL POWER | P-01-121
P-01-125 | 02E01 | 4 | 3 | #4/0 | XHHW-2 | 1 | #2 | XHHW-2 | FR: | MCC-CL |  |  |  | P-01-126
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-CL POWER | 0
P-01-126 | 02E01 | 4 | 3 | #4/0 | XHHW-2 | 1 | #2 | XHHW-2 | FR: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-CL POWER | P-01-125
P-01-141 | 02E01 | 4 | 3 | 500 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | SWBD-CS |  |  |  | P-01-151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 500 | >> | SWBD-CS POWER | 0
P-01-142 | 02E01 | 4 | 3 | 500 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | SWBD-CS |  |  |  | P-01-152
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 500 | >> | SWBD-CS POWER | 0
P-01-151 | 02E01 | 4 | 3 | 500 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | PB-12
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UNIT SUBSTATION
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 500 | >> | SWBD-CS POWER | P-01-141
P-01-152 | 02E01 | 4 | 3 | 500 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | PB-12
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UNIT SUBSTATION
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 500 | >> | SWBD-CS POWER | P-01-142
P-01-161 | 02E02 | 4 | 3 | #3/0 | XHHW-2 | 1 | #6 | XHHW-2 | FR: | PP-PAC
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
| 68E03 |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #3/0 | >> | PP-PAC POWER | 0
P-01-201 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-15 |  |  |  | P-01-202
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE POWER | 0
P-01-202 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE POWER | P-01-201
P-01-311 | 02E03 | 4 | 3 | 500 | XHHW-2 | 1 | #2/0 | XHHW-2 | FR: | PB #7
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 500 | >> | ATS MCC-A1 POWER (EXISTING CABLE) | 0
P-01-321 | 02E03 | 4 | 3 | 500 | XHHW-2 | 1 | #2/0 | XHHW-2 | FR: | PB #7
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 500 | >> | ATS MCC-A1 POWER (EXISTING CABLE) | 0
CONDUIT SCHEDULE AREA 01 | [12 empty] | ENGINEER | SKB
JORDAN VALLEY WATER TREATMENT PLANT | [12 empty] | REVISION | 0
SITE | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-01-331 | 02E03 | 4 | 3 | 500 | XHHW-2 | 1 | #2/0 | XHHW-2 | FR: | PB #7
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 500 | >> | ATS MCC-A1 POWER (NEW SPLICED CBL) | 0
P-01-411 | 01E05 | 4 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | MCC-WW |  |  |  | P-01-412
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #7 (VIA EXISTING DUCT BANK)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | MCC-WW POWER | 0
P-01-412 | 02E03 | 4 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | PB #7
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | MCC-WW POWER | P-01-411
P-01-421 | 01E05 | 4 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | MCC-WW |  |  |  | P-01-422
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #7 (VIA EXISTING DUCT BANK)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | MCC-WW POWER | 0
P-01-422 | 02E03 | 4 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | PB #7
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | MCC-WW POWER | P-01-421
P-01-431 | 02E03 | 4 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UNIT SUBSTATION
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | MCC-WW POWER (EXISTING CABLE) | 0
P-01-441 | 02E03 | 4 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UNIT SUBSTATION
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | MCC-WW POWER (EXISTING CABLE) | 0
P-01-521 | 01E02 | 2 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PB-18 (INTERCEPTED 480V WIRES TO CULINARY RESERVOIR)
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-RES
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | CULINARY RESERVOIR POWER (TEMP) | 0
X-01-011 | 02E03 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | XFMR CELL |  |  |  | X-01-012
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-17
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-012 | 02E03 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-17
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECTIONALIZER 2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-011
X-01-051 | 01E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SOUTH SECURITY GATE |  |  |  | X-01-052
| 02E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-052 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-15 |  |  |  | X-01-053
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-051
X-01-053 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | STUB UP IN CS BLDG ELEC ROOM
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-052
X-01-061 | 02E03 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SOUTH SECURITY GATE |  |  |  | X-01-062
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-062 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-15 |  |  |  | X-01-063
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-061
X-01-063 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | STUB-UP IN CS BLDG ELEC ROOM
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-062
X-01-071 | 01E02 | 5 | 1 | PULL | ROPE | 0 |  | 0 | FR: | RELOCATED PULLBOX
| 02E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-17
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-072 | 02E03 | 5 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-17
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECTIONALIZER 2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-094 | 02E03 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-APF
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-111 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | MCC-CS |  |  |  | X-01-112
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-112 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-14 |  |  |  | X-01-113
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-111
CONDUIT SCHEDULE AREA 01 | [12 empty] | ENGINEER | SKB
JORDAN VALLEY WATER TREATMENT PLANT | [12 empty] | REVISION | 0
SITE | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
X-01-113 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-112
X-01-115 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | MCC-CS |  |  |  | X-01-116
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-116 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-14 |  |  |  | X-01-117
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-115
X-01-117 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-116
X-01-131 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | MCC-CL |  |  |  | X-01-132
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-132 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-131
X-01-135 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | MCC-CL |  |  |  | X-01-136
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-136 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-135
X-01-143 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SWBD-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-144 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SWBD-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-153 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-12
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UNIT SUBSTATION
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-154 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-12
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UNIT SUBSTATION
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-171 | 02E02 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PAC ROOM
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | CHLORINE ELECTRICAL ROOM
| 68E03 |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-175 | 02E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PAC ROOM
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | CHLORINE ELECTRICAL ROOM
| 68E03 |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-213 | 01E02 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | HH-101 |  |  |  | X-01-214
| 02E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-214 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | STUB-UP IN CS BLDG ELEC ROOM
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-213
X-01-223 | 01E02 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | HH-101 |  |  |  | X-01-224
| 02E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-224 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | STUB-UP IN CS BLDG ELEC ROOM
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-01-223
X-01-301 | 02E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | STUB UP IN CS BLDG ELEC ROOM
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-311 | 02E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | STUB UP IN CHLORINE BLDG ELEC ROOM
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-321 | 02E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PAC ROOM
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | STUB UP IN CHLORINE BLDG ELEC ROOM
| 68E03 |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
CONDUIT SCHEDULE AREA 01 | [12 empty] | ENGINEER | SKB
JORDAN VALLEY WATER TREATMENT PLANT | [12 empty] | REVISION | 0
SITE | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
X-01-331 | 02E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-16
| 02E03 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-351 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-355 | 02E01 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | RTU-CL
| 63E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-461 | 02E03 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-471 | 02E03 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-481 | 02E03 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SWBD-APF
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB #7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-551 | 02E03 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-18
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-561 | 02E03 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-18
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-01-571 | 02E03 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-18
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
END OF CONDUIT SCHEDULE
END OF SECTION