## Print - Specs
SECTION 16990B
CONDUIT SCHEDULE
AREA 30
PART 1 GENERAL
1.01 SUMMARY
| A. |  | Conduit requirements:
1. As defined in Section 16050 and Section 16130.
| B. |  | Cable requirements and definitions:
1. As defined in Section 16050 and Section 16123.
|  |  | 2. 2/CS#16: |  |  |  | 2 conductor, 16 gauge, twisted shielded pair.
|  |  | 3. */FO: |  |  |  | Fiber optic (* indicates strand count).
|  |  | 4. CAT5e: |  |  |  | Category 5 enhanced Ethernet cable.
|  |  | 5. CAT6: |  |  |  | Category 6 Ethernet cable.
|  |  | 6. MFR: |  |  |  | Manufacturer or vendor furnished cable.
|  |  | 7. PULL: |  |  |  | Pull Rope.
|  |  | 8. RS-485 |  |  |  | RS-485 cable.
PART 2 PRODUCTS
Not Used.
PART 3 EXECUTION
3.01 CONDUIT SCHEDULE
| A. |  | Conduit Schedule is presented on the following pages.
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-010 | 30E03 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | MCC-BL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-BL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | MCC-BL CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | SPARE | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | SPD-3001 CONTROL | 0
C-30-101 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3010
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3010 CONTROL | 0
C-30-102 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3010
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3010 CONTROL | 0
C-30-103 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3011 CONTROL | 0
C-30-104 | 30E14 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3011 CONTROL | 0
C-30-105 | 30E14 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3011 CONTROL | 0
C-30-106 | 30E07 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3012
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3012 CONTROL | 0
C-30-107 | 30E06 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3013
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3013 CONTROL | 0
C-30-108 | 30E06 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3014
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3014
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3014 CONTROL | 0
C-30-109 | 30E06 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3014
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3014 CONTROL | 0
C-30-111 | 30E14 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3016
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3016 CONTROL | 0
C-30-112 | 30E14 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3017
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3017 CONTROL | 0
C-30-120 | 30E14 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3011 CONTROL POWER | 0
C-30-151 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3020
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3020 CONTROL | 0
C-30-152 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3020
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3020 CONTROL | 0
C-30-153 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3021 CONTROL | 0
C-30-154 | 30E18 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3021 CONTROL | 0
C-30-155 | 30E18 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3021 CONTROL | 0
C-30-156 | 30E07 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3022
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3022 CONTROL | 0
C-30-157 | 30E06 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3023
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3023 CONTROL | 0
C-30-158 | 30E06 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3024
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3024
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3024 CONTROL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-159 | 30E06 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3024
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3024 CONTROL/STATUS | 0
C-30-161 | 30E18 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3026
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3026 CONTROL | 0
C-30-162 | 30E18 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3027
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3027 CONTROL | 0
C-30-170 | 30E18 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3021 CONTROL | 0
C-30-201 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3030
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3030 CONTROL | 0
C-30-202 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3030
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3030 CONTROL | 0
C-30-203 | 30E07 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3031 CONTROL | 0
C-30-204 | 30E14 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3031 CONTROL | 0
C-30-205 | 30E14 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3031 CONTROL | 0
C-30-206 | 30E07 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3032
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3032 CONTROL | 0
C-30-207 | 30E06 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3033
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3033 CONTROL | 0
C-30-208 | 30E07 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3034
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3034
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3034 CONTROL | 0
C-30-209 | 30E06 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3034
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3034 CONTROL | 0
C-30-211 | 30E14 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3036
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3036 CONTROL | 0
C-30-212 | 30E14 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3037
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3037 CONTROL | 0
C-30-220 | 30E14 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3031 CONTROL | 0
C-30-251 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3040
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3040 CONTROL | 0
C-30-252 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3040
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3040 CONTROL | 0
C-30-253 | 30E07 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3041 CONTROL | 0
C-30-254 | 30E18 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3041 CONTROL | 0
C-30-255 | 30E18 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3041 CONTROL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-256 | 30E07 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3042
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3042 CONTROL | 0
C-30-257 | 30E06 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3043
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3043 CONTROL | 0
C-30-258 | 30E07 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3044
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3044
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3044 CONTROL | 0
C-30-259 | 30E06 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3044
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3044 CONTROL | 0
C-30-261 | 30E18 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3046
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3046 CONTROL | 0
C-30-262 | 30E18 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3047
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3047 CONTROL | 0
C-30-270 | 30E18 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3041 CONTROL | 0
C-30-301 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3050
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3050 CONTROL | 0
C-30-302 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3050
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3050 CONTROL | 0
C-30-303 | 30E07 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3051 CONTROL | 0
C-30-304 | 30E14 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3051 CONTROL | 0
C-30-305 | 30E14 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3051 CONTROL | 0
C-30-306 | 30E07 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3052
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3052 CONTROL | 0
C-30-307 | 30E06 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3053
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3053 CONTROL | 0
C-30-308 | 30E07 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3054
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3054
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3054 CONTROL | 0
C-30-309 | 30E06 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3054
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3054 CONTROL | 0
C-30-311 | 30E14 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3056
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3056 CONTROL | 0
C-30-312 | 30E14 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3057
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3057 CONTROL | 0
C-30-320 | 30E14 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3051 CONTROL | 0
C-30-351 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3060
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3060 CONTROL | 0
C-30-352 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3060
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3060 CONTROL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-353 | 30E07 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3061 CONTROL | 0
C-30-354 | 30E18 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3061 CONTROL | 0
C-30-355 | 30E18 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3061 CONTROL | 0
C-30-356 | 30E07 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3062
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3062 CONTROL | 0
C-30-357 | 30E06 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3063
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3063 CONTROL | 0
C-30-358 | 30E07 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3064
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3064
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3064 CONTROL | 0
C-30-359 | 30E06 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3064
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3064 CONTROL | 0
C-30-361 | 30E18 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3066
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3066 CONTROL | 0
C-30-362 | 30E18 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3067
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3067 CONTROL | 0
C-30-370 | 30E18 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3061 CONTROL | 0
C-30-401 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3070
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3070 CONTROL | 0
C-30-402 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3070
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3070 CONTROL | 0
C-30-403 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3071
| 30E13 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3071 CONTROL | 0
C-30-404 | 30E13 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3071 CONTROL | 0
C-30-405 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3071 CONTROL | 0
C-30-406 | 30E13 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3071 24VDC POWER | 0
C-30-407 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3072
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3072
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3072 CONTROL | 0
C-30-408 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3072
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3072 CONTROL | 0
C-30-410 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3073
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3073
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3073 CONTROL | 0
C-30-411 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3073
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3073 CONTROL | 0
C-30-413 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3074
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3074
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3074 CONTROL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-414 | 30E05 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3074
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3074 CONTROL | 0
C-30-417 | 30E13 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3076
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3076
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3076 CONTROL | 0
C-30-418 | 30E13 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3076
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3076 CONTROL | 0
C-30-420 | 30E13 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3077
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3077 CONTROL | 0
C-30-451 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3080
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3080 CONTROL | 0
C-30-452 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3080
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | RTU-SFL8 | 0
C-30-453 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3081
| 30E17 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3081 CONTROL | 0
C-30-454 | 30E17 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3081 CONTROL | 0
C-30-455 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3081 CONTROL | 0
C-30-456 | 30E17 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3081 24VDC POWER | 0
C-30-457 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3082
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3082
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3082 CONTROL | 0
C-30-458 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3082
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3082 CONTROL | 0
C-30-460 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3083
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3083
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3083 CONTROL | 0
C-30-461 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3083
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3083 CONTROL | 0
C-30-463 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3084
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3084
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3084 CONTROL | 0
C-30-464 | 30E05 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3084
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3084 CONTROL | 0
C-30-467 | 30E17 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3086
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3086
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3086 CONTROL | 0
C-30-468 | 30E17 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3086
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3086 CONTROL | 0
C-30-470 | 30E17 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3087
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3087 CONTROL | 0
C-30-501 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3090
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3090 CONTROL | 0
C-30-502 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3090
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3090 STATUS | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-503 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3091
| 30E13 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3091 CONTROL | 0
C-30-504 | 30E13 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3091 CONTROL | 0
C-30-505 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3091 CONTROL | 0
C-30-506 | 30E13 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3091 24VDC POWER | 0
C-30-507 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3092
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3092
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3092 CONTROL | 0
C-30-508 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3092
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3092 CONTROL | 0
C-30-510 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3093
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3093
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3093 CONTROL | 0
C-30-511 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3093
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3093 CONTROL | 0
C-30-513 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3094
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3094
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3094 CONTROL | 0
C-30-514 | 30E05 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3094
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3094 CONTROL | 0
C-30-517 | 30E13 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3096
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3096
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3096 CONTROL | 0
C-30-518 | 30E13 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3096
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3096 CONTROL | 0
C-30-520 | 30E13 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3097
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3097 CONTROL | 0
C-30-551 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3100
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3100 CONTROL | 0
C-30-552 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3100
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3100 STATUS | 0
C-30-553 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3101
| 30E17 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3101 CONTROL | 0
C-30-554 | 30E17 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3101 CONTROL | 0
C-30-555 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3101 CONTROL | 0
C-30-556 | 30E17 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | LIT-3101 CONTROL | 0
C-30-557 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3102
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3102
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3102 CONTROL | 0
C-30-558 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3102
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3102 CONTROL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-560 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3103
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3103 CONTROL | 0
C-30-561 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3103 CONTROL | 0
C-30-563 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3104
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3104
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3104 CONTROL | 0
C-30-564 | 30E05 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3104
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3104 CONTROL | 0
C-30-567 | 30E17 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3106
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3106
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3106 CONTROL | 0
C-30-568 | 30E17 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3106
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3106 CONTROL | 0
C-30-570 | 30E17 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3107
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3107 CONTROL | 0
C-30-601 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3110
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3110 CONTROL | 0
C-30-602 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3110
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3110 STATUS | 0
C-30-603 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3111
| 30E13 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3111 CONTROL | 0
C-30-604 | 30E13 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3111 CONTROL | 0
C-30-605 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3111 CONTROL | 0
C-30-606 | 30E13 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3111 24VDC POWER | 0
C-30-607 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3112
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3112
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3112 CONTROL | 0
C-30-608 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3112
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3112 CONTROL | 0
C-30-610 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3113
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3113
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3113 CONTROL | 0
C-30-611 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3113
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3113 CONTROL | 0
C-30-613 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3114
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3114
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3114 CONTROL | 0
C-30-614 | 30E05 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3114
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3114 CONTROL | 0
C-30-617 | 30E13 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3116
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3116
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3116 CONTROL | 0
C-30-618 | 30E13 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3116
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3116 CONTROL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-620 | 30E13 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3117
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3117 CONTROL | 0
C-30-651 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3120
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3120 CONTROL | 0
C-30-652 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3120
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3120 STATUS | 0
C-30-653 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3121
| 30E17 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3121 CONTROL | 0
C-30-654 | 30E17 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3121 CONTROL | 0
C-30-655 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3121 CONTROL | 0
C-30-656 | 30E17 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3121 24VDC POWER | 0
C-30-657 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3122
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3122
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3122 CONTROL | 0
C-30-658 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3122
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3122 CONTROL | 0
C-30-660 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3123
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3123
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3123 CONTROL | 0
C-30-661 | 30E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3123
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3123 CONTROL | 0
C-30-663 | 30E05 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3124
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3124
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3124 CONTROL | 0
C-30-664 | 30E05 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3124
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3124 CONTROL | 0
C-30-667 | 30E17 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3126
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3126
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3126 CONTROL | 0
C-30-668 | 30E17 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3126
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3126 CONTROL | 0
C-30-670 | 30E17 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3127
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3127 CONTROL | 0
C-30-691 | 30E19 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | FILTER 8 EXIT DOOR SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-30-695 | 30E19 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | FILTER 7 EXIT DOOR SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-30-698 | 30E19 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | LEVEL 1 TUNNEL DOOR SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-30-701 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3130
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3130 CONTROL | 0
C-30-702 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3130
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3130 CONTROL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-703 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3131
| 30E12 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3131 CONTROL | 0
C-30-704 | 30E12 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3131 CONTROL | 0
C-30-705 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3131 CONTROL | 0
C-30-706 | 30E12 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3131 24VDC POWER | 0
C-30-707 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3132
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3132
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3132 CONTROL | 0
C-30-708 | 30E04 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3132
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3132 CONTROL | 0
C-30-710 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3133
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3133
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3133 CONTROL | 0
C-30-711 | 30E04 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3133
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3133 CONTROL | 0
C-30-713 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3134
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3134
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3134 CONTROL | 0
C-30-714 | 30E04 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3134
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3134 CONTROL | 0
C-30-717 | 30E12 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3136
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3136
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3136 CONTROL | 0
C-30-718 | 30E12 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3136
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3136 CONTROL | 0
C-30-720 | 30E12 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3137
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3137 CONTROL | 0
C-30-751 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3140
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3140 CONTROL | 0
C-30-752 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3140
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3140 CONTROL | 0
C-30-753 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3141
| 30E16 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3141 CONTROL | 0
C-30-754 | 30E16 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3141 CONTROL | 0
C-30-755 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3141 CONTROL | 0
C-30-756 | 30E16 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3141 CONTROL POWER | 0
C-30-757 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3142
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3142
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3142 CONTROL | 0
C-30-758 | 30E04 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3142
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3142 CONTROL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-760 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3143
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3143
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3143 CONTROL | 0
C-30-761 | 30E04 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3143
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3143 CONTROL | 0
C-30-763 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3144
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3144
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3144 CONTROL | 0
C-30-764 | 30E04 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3144
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3144 CONTROL | 0
C-30-767 | 30E16 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3146
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3146
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3146 CONTROL | 0
C-30-768 | 30E16 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3146
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3146 CONTROL | 0
C-30-770 | 30E16 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3147
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3147 CONTROL | 0
C-30-801 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3150
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3150 CONTROL | 0
C-30-802 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3150
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3150 CONTROL | 0
C-30-803 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3151
| 30E12 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3151 CONTROL | 0
C-30-804 | 30E12 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3151 CONTROL | 0
C-30-805 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3151 CONTROL | 0
C-30-806 | 30E12 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3151 24VDC POWER | 0
C-30-807 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3152
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3152
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3152 CONTROL | 0
C-30-808 | 30E04 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3152
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3152 CONTROL | 0
C-30-810 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3153
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3153
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3153 CONTROL | 0
C-30-811 | 30E04 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3153
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3153 CONTROL | 0
C-30-813 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3154
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3154
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3154 CONTROL | 0
C-30-814 | 30E04 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3154
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3154 CONTROL | 0
C-30-817 | 30E12 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3156
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3156
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3156 CONTROL | 0
C-30-818 | 30E12 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3156
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3156 CONTROL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-820 | 30E12 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3157
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3157 CONTROL | 0
C-30-851 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3160
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3160 CONTROL | 0
C-30-852 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-3160
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-3160 CONTROL | 0
C-30-853 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-3161
| 30E16 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-3161 CONTROL | 0
C-30-854 | 30E16 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3161 CONTROL | 0
C-30-855 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-3161 CONTROL | 0
C-30-856 | 30E16 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3161 CONTROL | 0
C-30-857 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3162
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3162
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3162 CONTROL | 0
C-30-858 | 30E04 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3162
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3162 CONTROL | 0
C-30-860 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3163
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3163
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3163 CONTROL | 0
C-30-861 | 30E04 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3163
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3163 CONTROL | 0
C-30-863 | 30E04 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3164
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3164
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3164 CONTROL | 0
C-30-864 | 30E04 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3164
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3164 CONTROL | 0
C-30-867 | 30E16 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-3166
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3166
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-3166 CONTROL | 0
C-30-868 | 30E16 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3166
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FV-3166 CONTROL | 0
C-30-870 | 30E16 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-3167
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-3167 CONTROL | 0
C-30-901 | 30E05 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-3911
|  |  | 2 | #14 | XHHW-2 |  |  | 0 | TO: | MCC-A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-3911 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-3911 CONTROL | 0
C-30-902 | 30E05 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-3921
|  |  | 2 | #14 | XHHW-2 |  |  | 0 | TO: | MCC-A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-3921 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-3921 CONTROL | 0
C-30-906 | 30E07 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-4051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-ELEC2C
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-4051 CONTROL | 0
C-30-907 | 30E06 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-4051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-4051
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-4051 CONTROL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-30-908 | 30E07 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-4061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-ELEC2C
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-4061 CONTROL | 0
C-30-909 | 30E06 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-4061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-4061
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-4061 CONTROL | 0
C-30-910 | 30E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-4135
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-4135 CONTROL POWER | 0
C-30-911 | 30E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-4136
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-4136 CONTROL POWER | 0
C-30-912 | 30E02 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-4411
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | FV-4411 CONTROL | 0
C-30-913 | 30E02 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-4411
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-4411
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-4411 CONTROL | 0
C-30-914 | 30E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-4411
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-4411 24VDC CONTROL POWER | 0
C-30-915 | 01E04 | 1 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-4425
| 01E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-BL
| 30E03 |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-4425 CONTROL | 0
C-30-916 | 01E04 | 1 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSHH-4427
| 01E05 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-BL
| 30E03 |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSHH-4427 CONTROL | 0
C-30-930 | 30E13 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3001
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3001 CONTROL POWER | 0
C-30-932 | 30E17 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LIT-3002
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-3002 CONTROL | 0
C-30-951 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSHH-3931
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSHH-3931 STATUS | 0
C-30-952 | 30E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-3942
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSH-3942 STATUS | 0
L-30-005 | 30E03 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | RTU-BL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UPS-S
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | RTU-BL POWER | 0
L-30-691 | 30E19 | 1 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-B1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SECURITY PANEL POWER | 0
L-30-695 | 30E19 | 1 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UPS-B
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SECURITY PANEL POWER | 0
L-30-696 | 30E19 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | LOI-FB
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UPS-B
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | LOI-FB POWER | 0
L-30-950 | 30E05 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-3931
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PANELBOARD FGA, CKT 5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-3931 POWER | 0
L-30-951 | 30E05 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-3941
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PANELBOARD FGA, CKT 7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-3941 POWER | 0
N-30-005 | 30E03 | 2 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | RTU-BL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LEVEL 2 NETWORK ROOM
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | RTU-BL NETWORK | 0
N-30-010 | 30E03 | 0.75 | 1 | 0 | CAT5E | 1 | #14 | XHHW-2 | FR: | MCC-BL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-BL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT5E | >> | MCC-BL NETWORK | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
N-30-101 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3010
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3010 NETWORK | 0
N-30-102 | 30E06 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3011 NETWORK | 0
N-30-103 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3019
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3019 NETWORK | 0
N-30-151 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3020
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3020 NETWORK | 0
N-30-152 | 30E06 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3021 NETWORK | 0
N-30-153 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3029
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3029 NETWORK | 0
N-30-201 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3030
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3030 NETWORK | 0
N-30-202 | 30E07 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3031 NETWORK | 0
N-30-203 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3039
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3039 NETWORK | 0
N-30-251 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3040
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3040 NETWORK | 0
N-30-252 | 30E07 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3041 NETWORK | 0
N-30-253 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3049
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3049 NETWORK | 0
N-30-301 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3050
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3050 NETWORK | 0
N-30-302 | 30E07 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3051 NETWORK | 0
N-30-303 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3059
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3059 NETWORK | 0
N-30-351 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3060
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3060 NETWORK | 0
N-30-352 | 30E07 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3061 NETWORK | 0
N-30-353 | 30E06 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3069
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3069 NETWORK | 0
N-30-401 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3070
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3070 NETWORK | 0
N-30-402 | 30E05 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3071 NETWORK | 0
N-30-403 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3079
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3079 NETWORK | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
N-30-451 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3080
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3080 NETWORK | 0
N-30-452 | 30E05 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3081 NETWORK | 0
N-30-453 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3089
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3089 NETWORK | 0
N-30-501 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3090
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3090 NETWORK | 0
N-30-502 | 30E05 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3091 NETWORK | 0
N-30-503 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3099
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3099 NETWORK | 0
N-30-551 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3100
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3100 NETWORK | 0
N-30-552 | 30E05 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3101 NETWORK | 0
N-30-553 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3109
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3109 NETWORK | 0
N-30-601 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3110
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3110 NETWORK | 0
N-30-602 | 30E05 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3111 NETWORK | 0
N-30-603 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3119
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3119 NETWORK | 0
N-30-651 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3120
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3120 NETWORK | 0
N-30-652 | 30E05 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3121 NETWORK | 0
N-30-653 | 30E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3129
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3129 NETWORK | 0
N-30-691 | 30E19 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | NETWORK RACK
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-30-695 | 30E19 | 1 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | LOI-FB
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | NETWORK ROOM FIBER PATCH PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | LOI-FB NETWORK | 0
N-30-701 | 30E04 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3130
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3130 NETWORK | 0
N-30-702 | 30E04 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3131 NETWORK | 0
N-30-703 | 30E04 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3139
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3139 NETWORK | 0
N-30-751 | 30E04 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3140
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3140 NETWORK | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
N-30-752 | 30E04 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3141 NETWORK | 0
N-30-753 | 30E04 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3149
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3149 NETWORK | 0
N-30-801 | 30E04 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3150
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3150 NETWORK | 0
N-30-802 | 30E04 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3151 NETWORK | 0
N-30-803 | 30E04 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3159
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3159 NETWORK | 0
N-30-851 | 30E04 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3160
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3160 NETWORK | 0
N-30-852 | 30E04 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-3161 NETWORK | 0
N-30-853 | 30E04 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | AIT-3169
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | AIT-3169 NETWORK | 0
N-30-902 | 30E04 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-4135
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-4135 MBRTU | 0
N-30-904 | 30E02 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-4411
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-4411 NETWORK | 0
P-30-011 | 30E03 | 3 | 3 | 300 | XHHW-2 | 1 | #1/0 | XHHW-2 | FR: | BLO-4201
|  |  | 2 | #12 | XHHW-2 |  |  | 0 | TO: | MCC-BL
|  |  | 2 | #14 | XHHW-2 |  |  | 0 |  | 3 | 300 | >> | BLO-4201 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | BLO-4201 MWH POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | BLO-4201 TSH CONTROL | 0
P-30-012 | 30E03 | 3 | 3 | 300 | XHHW-2 | 1 | #1/0 | XHHW-2 | FR: | BLO-4201
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-BL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 300 | >> | BLO-4201 POWER | 0
P-30-021 | 30E03 | 3 | 3 | 300 | XHHW-2 | 1 | #1/0 | XHHW-2 | FR: | BLO-4211
|  |  | 2 | #12 | XHHW-2 |  |  | 0 | TO: | MCC-BL
|  |  | 2 | #14 | XHHW-2 |  |  | 0 |  | 3 | 300 | >> | BLO-4211 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | BLO-4211 MWH POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | BLO-4211 TSH CONTROL | 0
P-30-022 | 30E03 | 3 | 3 | 300 | XHHW-2 | 1 | #1/0 | XHHW-2 | FR: | BLO-4211
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-BL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 300 | >> | BLO-4211 POWER | 0
P-30-101 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3011
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3011 POWER | 0
P-30-102 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3012
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3012
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3012 POWER | 0
P-30-103 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3013
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3013
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3013 POWER | 0
P-30-104 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3014
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3014
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3014 POWER | 0
P-30-106 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3016
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3016
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3016 POWER | 0
P-30-107 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3017
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3017
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3017 POWER | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-30-111 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3011 POWER | 0
P-30-112 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3012
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3012 POWER | 0
P-30-113 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3013
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3013 POWER | 0
P-30-114 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3014
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3014 POWER | 0
P-30-116 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3016
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3016 POWER | 0
P-30-117 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3017
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3017 POWER | 0
P-30-151 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3021
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3021 POWER | 0
P-30-152 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3022
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3022
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3022 POWER | 0
P-30-153 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3023
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3023
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3023 POWER | 0
P-30-154 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3024
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3024
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3024 POWER | 0
P-30-156 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3026
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3026
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3026 POWER | 0
P-30-157 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3027
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3027
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3027 POWER | 0
P-30-161 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3021 POWER | 0
P-30-162 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3022
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3022 POWER | 0
P-30-163 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3023
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3023 POWER | 0
P-30-164 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3024
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3024 POWER | 0
P-30-166 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3026
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3026 POWER | 0
P-30-167 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3027
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3027 POWER | 0
P-30-201 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3031
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3031 POWER | 0
P-30-202 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3032
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3032
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3032 POWER | 0
P-30-203 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3033
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3033
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3033 POWER | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-30-204 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3034
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3034
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3034 POWER | 0
P-30-206 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3036
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3036
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3036 POWER | 0
P-30-207 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3037
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3037
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3037 POWER | 0
P-30-211 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3031 POWER | 0
P-30-212 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3032
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3032 POWER | 0
P-30-213 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3033
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3033 POWER | 0
P-30-214 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3034
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3034 POWER | 0
P-30-216 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3036
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3036 POWER | 0
P-30-217 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3037
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3037 POWER | 0
P-30-251 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3041
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3041 POWER | 0
P-30-252 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3042
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3042
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3042 POWER | 0
P-30-253 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3043
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3043
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3043 POWER | 0
P-30-254 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3044
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3044
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3044 POWER | 0
P-30-256 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3046
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3046
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3046 POWER | 0
P-30-257 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3047
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3047
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3047 POWER | 0
P-30-261 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3041 POWER | 0
P-30-262 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3042
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3042 POWER | 0
P-30-263 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3043
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3043 POWER | 0
P-30-264 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3044
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3044 POWER | 0
P-30-266 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3046
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3046 POWER | 0
P-30-267 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3047
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3047 POWER | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-30-301 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3051
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3051 POWER | 0
P-30-302 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3052
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3052
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3052 POWER | 0
P-30-303 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3053
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3053
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3053 POWER | 0
P-30-304 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3054
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3054
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3054 POWER | 0
P-30-306 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3056
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3056
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3056 POWER | 0
P-30-307 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3057
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3057
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3057 POWER | 0
P-30-311 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3051 POWER | 0
P-30-312 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3052
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3052 POWER | 0
P-30-313 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3053
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3053 POWER | 0
P-30-314 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3054
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3054 POWER | 0
P-30-316 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3056
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3056 POWER | 0
P-30-317 | 30E14 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3057
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3057 POWER | 0
P-30-351 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3061
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3061 POWER | 0
P-30-352 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3062
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3062
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3062 POWER | 0
P-30-353 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3063
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3063
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3063 POWER | 0
P-30-354 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3064
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3064
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3064 POWER | 0
P-30-356 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3066
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3066
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3066 POWER | 0
P-30-357 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3067
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3067
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3067 POWER | 0
P-30-361 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3061 POWER | 0
P-30-362 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3062
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3062 POWER | 0
P-30-363 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3063
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3063 POWER | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-30-364 | 30E07 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3064
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3064 POWER | 0
P-30-366 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3066
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3066 POWER | 0
P-30-367 | 30E18 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3067
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3067 POWER | 0
P-30-401 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3071
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3071 POWER | 0
P-30-402 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3072
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3072
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3072 POWER | 0
P-30-403 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3073
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3073
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3073 POWER | 0
P-30-404 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3074
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3074
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3074 POWER | 0
P-30-406 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3076
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3076
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3076 POWER | 0
P-30-407 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3077
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3077
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3077 POWER | 0
P-30-411 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3071 POWER | 0
P-30-412 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3072
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3072 POWER | 0
P-30-413 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3073
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3073 POWER | 0
P-30-414 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3074
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3074 POWER | 0
P-30-416 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3076
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3076 POWER | 0
P-30-417 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3077
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3077 POWER | 0
P-30-451 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3081
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3081 POWER | 0
P-30-452 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3082
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3082
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3082 POWER | 0
P-30-453 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3083
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3083
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3083 POWER | 0
P-30-454 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3084
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3084
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3084 POWER | 0
P-30-456 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3086
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3086
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3086 POWER | 0
P-30-457 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3087
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3087
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3087 POWER | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-30-461 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3081 POWER | 0
P-30-462 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3082
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3082 POWER | 0
P-30-463 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3083
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3083 POWER | 0
P-30-464 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3084
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3084 POWER | 0
P-30-466 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3086
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3086 POWER | 0
P-30-467 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3087
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3087 POWER | 0
P-30-501 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3091
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3091 POWER | 0
P-30-502 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3092
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3092
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3092 POWER | 0
P-30-503 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3093
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3093
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3093 POWER | 0
P-30-504 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3094
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3094
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3094 POWER | 0
P-30-506 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3096
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3096
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3096 POWER | 0
P-30-507 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3097
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3097
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3097 POWER | 0
P-30-511 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3091 POWER | 0
P-30-512 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3092
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3092 POWER | 0
P-30-513 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3093
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3093 POWER | 0
P-30-514 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3094
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3094 POWER | 0
P-30-516 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3096
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3096 POWER | 0
P-30-517 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3097
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3097 POWER | 0
P-30-551 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3101
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3101 POWER | 0
P-30-552 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3102
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3102
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3102 POWER | 0
P-30-553 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3103
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3103 POWER | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-30-554 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3104
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3104
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3104 POWER | 0
P-30-556 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3106
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3106
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3106 POWER | 0
P-30-557 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3107
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3107
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3107 POWER | 0
P-30-561 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3101 POWER | 0
P-30-562 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3102
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3102 POWER | 0
P-30-563 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3103 POWER | 0
P-30-564 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3104
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3104 POWER | 0
P-30-566 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3106
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3106 POWER | 0
P-30-567 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3107
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3107 POWER | 0
P-30-601 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3111
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3111 POWER | 0
P-30-602 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3112
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3112
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3112 POWER | 0
P-30-603 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3113
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3113
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3113 POWER | 0
P-30-604 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3114
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3114
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3114 POWER | 0
P-30-606 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3116
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3116
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3116 POWER | 0
P-30-607 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3117
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3117
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3117 POWER | 0
P-30-611 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3111 POWER | 0
P-30-612 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3112
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3112 POWER | 0
P-30-613 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3113
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3113 POWER | 0
P-30-614 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3114
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3114 POWER | 0
P-30-616 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3116
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3116 POWER | 0
P-30-617 | 30E13 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3117
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3117 POWER | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-30-651 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3121
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3121 POWER | 0
P-30-652 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3122
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3122
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3122 POWER | 0
P-30-653 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3123
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3123
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3123 POWER | 0
P-30-654 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3124
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3124
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3124 POWER | 0
P-30-656 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3126
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3126
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3126 POWER | 0
P-30-657 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3127
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3127
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3127 POWER | 0
P-30-661 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3121 POWER | 0
P-30-662 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3122
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3122 POWER | 0
P-30-663 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3123
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3123 POWER | 0
P-30-664 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3124
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3124 POWER | 0
P-30-666 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3126
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3126 POWER | 0
P-30-667 | 30E17 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3127
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3127 POWER | 0
P-30-701 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3131
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3131 POWER | 0
P-30-702 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3132
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3132
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3132 POWER | 0
P-30-703 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3133
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3133
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3133 POWER | 0
P-30-704 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3134
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3134
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3134 POWER | 0
P-30-706 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3136
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3136
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3136 POWER | 0
P-30-707 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3137
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3137
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3137 POWER | 0
P-30-711 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3131 POWER | 0
P-30-712 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3132
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3132 POWER | 0
P-30-713 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3133
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3133 POWER | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-30-714 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3134
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3134 POWER | 0
P-30-716 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3136
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3136 POWER | 0
P-30-717 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3137
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3137 POWER | 0
P-30-751 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3141
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3141 POWER | 0
P-30-752 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3142
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3142
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3142 POWER | 0
P-30-753 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3143
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3143
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3143 POWER | 0
P-30-754 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3144
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3144
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3144 POWER | 0
P-30-756 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3146
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3146
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3146 POWER | 0
P-30-757 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3147
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3147
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3147 POWER | 0
P-30-761 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3141 POWER | 0
P-30-762 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3142
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3142 POWER | 0
P-30-763 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3143
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3143 POWER | 0
P-30-764 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3144
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3144 POWER | 0
P-30-766 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3146
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3146 POWER | 0
P-30-767 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3147
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3147 POWER | 0
P-30-801 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3151
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3151 POWER | 0
P-30-802 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3152
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3152
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3152 POWER | 0
P-30-803 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3153
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3153
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3153 POWER | 0
P-30-804 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3154
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3154
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3154 POWER | 0
P-30-806 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3156
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3156
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3156 POWER | 0
P-30-807 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3157
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3157
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3157 POWER | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-30-811 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3151 POWER | 0
P-30-812 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3152
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3152 POWER | 0
P-30-813 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3153
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3153 POWER | 0
P-30-814 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3154
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3154 POWER | 0
P-30-816 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3156
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3156 POWER | 0
P-30-817 | 30E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3157
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3157 POWER | 0
P-30-851 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3161
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3161 POWER | 0
P-30-852 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3162
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3162
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3162 POWER | 0
P-30-853 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3163
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3163
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3163 POWER | 0
P-30-854 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3164
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3164
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3164 POWER | 0
P-30-856 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3166
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3166
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3166 POWER | 0
P-30-857 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3167
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-3167
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-3167 POWER | 0
P-30-861 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3161 POWER | 0
P-30-862 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3162
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3162 POWER | 0
P-30-863 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3163
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3163 POWER | 0
P-30-864 | 30E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3164
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3164 POWER | 0
P-30-866 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3166
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3166 POWER | 0
P-30-867 | 30E16 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-3167
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-3167 POWER | 0
P-30-901 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-3911
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PMP-3911 POWER | 0
P-30-902 | 30E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-3921
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PMP-3921 POWER | 0
P-30-904 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-4051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-4051
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4051 POWER | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-30-905 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-4061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-4061
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4061 POWER | 0
P-30-906 | 30E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-4411
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FV-4411
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | FV-4411 POWER | 0
P-30-914 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-4051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-4051 POWER | 0
P-30-915 | 30E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-4061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-4061 POWER | 0
P-30-916 | 30E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-4411
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | DISC-4411 POWER | 0
S-30-102 | 30E06 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3011
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3011 SIGNAL | 0
S-30-103 | 30E14 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3011
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3011 SIGNAL | 0
S-30-104 | 30E14 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3011 SIGNAL | 0
S-30-105 | 30E14 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3011 SIGNAL | 0
S-30-106 | 30E06 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3011 SIGNAL | 0
S-30-107 | 30E07 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3012
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3012 SIGNAL | 0
S-30-108 | 30E06 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3013
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3013 SIGNAL | 0
S-30-110 | 30E14 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3011
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3011 SIGNAL | 0
S-30-111 | 30E14 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3011
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-3011 SIGNAL | 0
S-30-112 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3010
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3010
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3010 SIGNAL | 0
S-30-113 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3019
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3019
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3019 SIGNAL | 0
S-30-152 | 30E06 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3021
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3021 SIGNAL | 0
S-30-153 | 30E18 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3021
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3021 SIGNAL | 0
S-30-154 | 30E18 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3021 SIGNAL | 0
S-30-155 | 30E18 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3021 SIGNAL | 0
S-30-156 | 30E06 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3021 SIGNAL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-30-157 | 30E07 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3022
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3022 SIGNAL | 0
S-30-158 | 30E06 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3023
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3023 SIGNAL | 0
S-30-160 | 30E18 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3021
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3021 SIGNAL | 0
S-30-161 | 30E18 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3021
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL2
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3021 SIGNAL | 0
S-30-162 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3020
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3020
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3020 SIGNAL | 0
S-30-163 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3029
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3029
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3029 SIGNAL | 0
S-30-202 | 30E06 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3031
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3031 SIGNAL | 0
S-30-203 | 30E14 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3031
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3031 SIGNAL | 0
S-30-204 | 30E14 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3031 SIGNAL | 0
S-30-205 | 30E14 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3031 SIGNAL | 0
S-30-206 | 30E06 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | PIT-3031 SIGNAL | 0
S-30-207 | 30E07 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3032
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3032 SIGNAL | 0
S-30-208 | 30E06 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3033
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3033 SIGNAL | 0
S-30-210 | 30E14 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3031
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3031 SIGNAL | 0
S-30-211 | 30E14 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3031
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL3
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-3031 SIGNAL | 0
S-30-212 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3030
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3030
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3030 SIGNAL | 0
S-30-213 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3039
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3039
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3039 SIGNAL | 0
S-30-252 | 30E06 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3041
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3041 SIGNAL | 0
S-30-253 | 30E18 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3041
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3041 SIGNAL | 0
S-30-254 | 30E18 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3041 SIGNAL | 0
S-30-255 | 30E18 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3041 SIGNAL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-30-256 | 30E06 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3041 SIGNAL | 0
S-30-257 | 30E07 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3042
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | FV-3042 SIGNAL | 0
S-30-258 | 30E06 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3043
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3043 SIGNAL | 0
S-30-260 | 30E18 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3041
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3041 SIGNAL | 0
S-30-261 | 30E18 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3041
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL4
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-3041 SIGNAL | 0
S-30-262 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3040
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3040
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3040 SIGNAL | 0
S-30-263 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3049
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3049
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3049 SIGNAL | 0
S-30-302 | 30E06 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3051
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3051 SIGNAL | 0
S-30-303 | 30E14 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3051
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3051 SIGNAL | 0
S-30-304 | 30E14 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3051 SIGNAL | 0
S-30-305 | 30E14 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3051 SIGNAL | 0
S-30-306 | 30E06 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3051 SIGNAL | 0
S-30-307 | 30E07 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3052
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3052 SIGNAL | 0
S-30-308 | 30E06 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3053
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3053 SIGNAL | 0
S-30-310 | 30E14 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3051
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3051 SIGNAL | 0
S-30-311 | 30E14 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL5
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-3051 SIGNAL | 0
S-30-312 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3050
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3050
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3050 SIGNAL | 0
S-30-313 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3059
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3059
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3059 SIGNAL | 0
S-30-352 | 30E06 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3061
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3061 SIGNAL | 0
S-30-353 | 30E18 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3061
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3061 SIGNAL | 0
S-30-354 | 30E18 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3061 SIGNAL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-30-355 | 30E18 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3061 SIGNAL | 0
S-30-356 | 30E06 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3061 SIGNAL | 0
S-30-357 | 30E07 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3062
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3062 SIGNAL | 0
S-30-358 | 30E06 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3063
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3063 SIGNAL | 0
S-30-360 | 30E18 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3061
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3061 SIGNAL | 0
S-30-361 | 30E18 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL6
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3061 SIGNAL | 0
S-30-362 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3060
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3060
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3060 SIGNAL | 0
S-30-363 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3069
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3069
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3069 SIGNAL | 0
S-30-402 | 30E13 | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3071
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3071 SIGNAL | 0
S-30-403 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3071
| 30E13 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3071 SIGNAL | 0
S-30-404 | 30E05 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3071
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3071 SIGNAL | 0
S-30-405 | 30E13 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3071
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3071 SIGNAL | 0
S-30-406 | 30E13 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | LIT-3071 SIGNAL | 0
S-30-407 | 30E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3071
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3071 SIGNAL | 0
S-30-408 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3072
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3072 SIGNAL | 0
S-30-409 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3073
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3073 SIGNAL | 0
S-30-410 | 30E13 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3077
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL7
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3077 SIGNAL | 0
S-30-412 |  | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3070
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3070
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3070 SIGNAL | 0
S-30-413 |  | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3079
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3079
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3079 SIGNAL | 0
S-30-452 | 30E17 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3081
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3081 SIGNAL | 0
S-30-453 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3081
| 30E17 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3081 SIGNAL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-30-454 | 30E05 | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3081
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | FE-3081 SIGNAL | 0
S-30-455 | 30E17 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3081
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3081 SIGNAL | 0
S-30-456 | 30E17 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3081 SIGNAL | 0
S-30-457 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3081
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | PIT-3081 SIGNAL | 0
S-30-458 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3082
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3082 SIGNAL | 0
S-30-459 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3083
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3083 SIGNAL | 0
S-30-460 | 30E17 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3087
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL8
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3087 SIGNAL | 0
S-30-462 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3080
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3080
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3080 SIGNAL | 0
S-30-463 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3089
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3089
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3089 SIGNAL | 0
S-30-502 | 30E13 | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3091
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3091 SIGNAL | 0
S-30-503 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3091
| 30E13 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3091 SIGNAL | 0
S-30-504 | 30E05 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3091
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3091 SIGNAL | 0
S-30-505 | 30E13 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3091
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3091 SIGNAL | 0
S-30-506 | 30E13 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | LIT-3091 SIGNAL | 0
S-30-507 | 30E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3091
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3091 SIGNAL | 0
S-30-508 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3092
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3092 SIGNAL | 0
S-30-509 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3093
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3093 SIGNAL | 0
S-30-510 | 30E13 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3097
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL9
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3097 SIGNAL | 0
S-30-512 |  | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3090
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3090
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3090 SIGNAL | 0
S-30-513 |  | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3099
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3099
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3099 SIGNAL | 0
S-30-552 | 30E17 | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3101
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3101 SIGNAL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-30-553 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3101
| 30E17 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3101 SIGNAL | 0
S-30-554 | 30E05 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3101
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3101 SIGNAL | 0
S-30-555 | 30E17 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3101
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3101 SIGNAL | 0
S-30-556 | 30E17 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3101 SIGNAL | 0
S-30-557 | 30E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3101 SIGNAL | 0
S-30-558 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3102
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3102 SIGNAL | 0
S-30-559 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3103 SIGNAL | 0
S-30-560 | 30E17 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3107
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL10
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3107 SIGNAL | 0
S-30-562 |  | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3100
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3100
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3100 | 0
S-30-563 |  | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3109
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3109
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3109 | 0
S-30-602 | 30E13 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3111
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3111 SIGNAL | 0
S-30-603 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3111
| 30E13 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3111 SIGNAL | 0
S-30-604 | 30E05 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3111
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3111 SIGNAL | 0
S-30-605 | 30E13 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3111
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3111 SIGNAL | 0
S-30-606 | 30E13 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3111 SIGNAL | 0
S-30-607 | 30E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3111
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3111 SIGNAL | 0
S-30-608 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3112
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3112 SIGNAL | 0
S-30-609 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3113
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3113 SIGNAL | 0
S-30-610 | 30E13 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3117
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL11
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3117 SIGNAL | 0
S-30-612 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3110
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3110
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3110 SIGNAL | 0
S-30-613 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3119
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3119
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3119 SIGNAL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-30-652 | 30E17 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3121
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3121 SIGNAL | 0
S-30-653 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3121
| 30E17 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3121 SIGNAL | 0
S-30-654 | 30E05 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3121
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3121 SIGNAL | 0
S-30-655 | 30E17 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3121
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3121 SIGNAL | 0
S-30-656 | 30E17 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3121 SIGNAL | 0
S-30-657 | 30E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3121
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3121 SIGNAL | 0
S-30-658 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3122
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3122 SIGNAL | 0
S-30-659 | 30E05 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3123
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3123 SIGNAL | 0
S-30-660 | 30E17 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3127
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL12
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3127 SIGNAL | 0
S-30-662 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3120
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3120
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3120 SIGNAL | 0
S-30-663 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3129
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3129
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3129 SIGNAL | 0
S-30-702 | 30E12 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3131
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3131 SIGNAL | 0
S-30-703 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3131
| 30E12 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3131 SIGNAL | 0
S-30-704 | 30E04 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3131
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3131 SIGNAL | 0
S-30-705 | 30E12 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3131
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3131 SIGNAL | 0
S-30-706 | 30E12 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3131 SIGNAL | 0
S-30-707 | 30E04 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3131
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3131 SIGNAL | 0
S-30-708 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3132
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3132 SIGNAL | 0
S-30-709 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3133
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3133 SIGNAL | 0
S-30-710 | 30E12 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3137
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL13
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3137 SIGNAL | 0
S-30-712 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3130
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3130
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3130 SIGNAL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-30-713 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3139
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3139
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3139 SIGNAL | 0
S-30-752 | 30E16 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3141
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3141 SIGNAL | 0
S-30-753 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3141
| 30E16 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3141 SIGNAL | 0
S-30-754 | 30E04 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3141
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3141 SIGNAL | 0
S-30-755 | 30E16 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3141
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3141 SIGNAL | 0
S-30-756 | 30E16 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3141 SIGNAL | 0
S-30-757 | 30E04 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3141
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3141 SIGNAL | 0
S-30-758 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3142
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3142 SIGNAL | 0
S-30-759 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3143
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3143 SIGNAL | 0
S-30-760 | 30E16 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3147
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3147 SIGNAL | 0
S-30-762 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3140
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3140
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3140 SIGNAL | 0
S-30-763 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3149
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3149
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3149 SIGNAL | 0
S-30-802 | 30E12 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3151
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3151 SIGNAL | 0
S-30-803 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3151
| 30E12 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3151 SIGNAL | 0
S-30-804 | 30E04 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3151
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3151 SIGNAL | 0
S-30-805 | 30E12 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3151
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3151 SIGNAL | 0
S-30-806 | 30E12 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3151 SIGNAL | 0
S-30-807 | 30E04 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3151
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3151 SIGNAL | 0
S-30-808 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3152
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3152 SIGNAL | 0
S-30-809 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3153
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3153 SIGNAL | 0
S-30-810 | 30E12 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3157
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-NFL15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3157 SIGNAL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-30-812 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3150
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3150
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3150 SIGNAL | 0
S-30-813 |  | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3159
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3159
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AE-3159 SIGNAL | 0
S-30-852 | 30E16 | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3161
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3161 SIGNAL | 0
S-30-853 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | AIT-3161
| 30E16 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | AIT-3161 SIGNAL | 0
S-30-854 | 30E04 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-3161
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-3161 SIGNAL | 0
S-30-855 | 30E16 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3161
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3161 SIGNAL | 0
S-30-856 | 30E16 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3161 SIGNAL | 0
S-30-857 | 30E04 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PIT-3161
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PIT-3161 SIGNAL | 0
S-30-858 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3162
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3162 SIGNAL | 0
S-30-859 | 30E04 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3163
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3163 SIGNAL | 0
S-30-860 | 30E16 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-3167
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-SFL16
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-3167 SIGNAL | 0
S-30-862 |  | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3160
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3160
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3160 SIGNAL | 0
S-30-863 |  | 0.75 | 2 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AE-3169
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AIT-3169
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | MFR | >> | AE-3169 SIGNAL | 0
S-30-903 | 30E07 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-4051
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-ELEC2C
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-4051 SIGNAL | 0
S-30-904 | 30E07 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-4061
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-ELEC2C
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-4061 SIGNAL | 0
S-30-905 | 30E04 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-4135
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-4135
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-4135 SIGNAL | 0
S-30-906 | 30E07 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-4136
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-4136
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-4136 SIGNAL | 0
S-30-907 | 30E02 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FV-4411
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | FV-4411 SIGNAL | 0
S-30-908 | 30E02 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | FE-4411
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FIT-4411
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | FE-4411 SIGNAL | 0
S-30-914 | 30E06 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FIT-4136
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | FIT-4136 SIGNAL | 0
S-30-930 | 30E13 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3001
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3001
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3001 SIGNAL | 0
CONDUIT SCHEDULE AREA | [12 empty] | ENGINEER | AJB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
FILTERS | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-30-931 | 30E13 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3001
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3001 SIGNAL | 0
S-30-932 | 30E17 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-3002
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-3002
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-3002 SIGNAL | 0
S-30-933 | 30E17 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-3002
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FBW
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-3002 SIGNAL | 0
END OF CONDUIT SCHEDULE
END OF SECTION