## Print - Specs
SECTION 16990C
CONDUIT SCHEDULE
AREA 41
PART 1 GENERAL
1.01 SUMMARY
| A. |  | Conduit requirements:
1. As defined in Section 16050 and Section 16130.
| B. |  | Cable requirements and definitions:
1. As defined in Section 16050 and Section 16123.
|  |  | 2. 2/CS#16: |  |  |  | 2 conductor, 16 gauge, twisted shielded pair.
|  |  | 3. */C#Y: |  |  |  | Multiconductor cable (* indicates number of
conductors, Y indicates conductor size and insulation).
|  |  | 4. MFR: |  |  |  | Manufacturer or vendor furnished cable.
|  |  | 5. PULL: |  |  |  | Pull Rope.
|  |  | 6. VFD: |  |  |  | Shielded VFD cable with integral ground.
PART 2 PRODUCTS
Not Used.
PART 3 EXECUTION
3.01 CONDUIT SCHEDULE
| A. |  | Conduit Schedule is presented on the following pages.
CONDUIT SCHEDULE AREA 41 | [12 empty] | ENGINEER | SKB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
BACKWASH TANK AND VAULT | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-41-115 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | STUB-UP AT BACKWASH TANK
| 41E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-41-211 | 41E01 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-4112 |  |  |  | C-41-226
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-4112 CONTROL | 0
C-41-221 | 41E01 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-4122 |  |  |  | C-41-226
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-4122 CONTROL | 0
C-41-225 | 41E01 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSHH-4123 |  |  |  | C-41-226
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSHH-4123 CONTROL | 0
C-41-226 | 02E01 | 2 | 22 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | J-BOX |  |  |  | C-41-227
| 41E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-4112 CONTROL | C-41-211
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-4122 CONTROL | C-41-221
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSHH-4123 CONTROL | C-41-225
C-41-227 | 02E01 | 2 | 22 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PB-15 |  |  |  | C-41-228
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-4112 CONTROL | C-41-226
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-4122 CONTROL | C-41-226
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSHH-4123 CONTROL | C-41-226
C-41-228 | 02E01 | 2 | 22 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-4112 CONTROL | C-41-227
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-4122 CONTROL | C-41-227
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSHH-4123 CONTROL | C-41-227
C-41-412 | 30E09 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VFD-4101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-ELEC1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VFD-4101 CONTROL (120VAC) | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | SPARE | 0
C-41-415 | 30E09 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VFD-4101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-ELEC1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 5 | #14 | >> | VFD-4101 CONTROL (24VDC) | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | SPARE | 0
C-41-422 | 30E09 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VFD-4102
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-ELEC1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VFD-4102 CONTROL (120VAC) | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | SPARE | 0
C-41-425 | 30E09 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VFD-4102
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-ELEC1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 5 | #14 | >> | VFD-4102 CONTROL (24VDC) | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | SPARE | 0
L-41-224 | 41E01 | 1 | 2 | #4 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | PMP-4125 |  |  |  | L-41-225
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #4 | >> | PMP-4125 POWER | 0
L-41-225 | 02E01 | 2 | 2 | #4 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | J-BOX |  |  |  | L-41-226
| 41E01 |  | 2 | #6 | XHHW-2 |  |  | 0 | TO: | PB-15
|  |  | 4 | #12 | XHHW-2 |  |  | 0 |  | 2 | #4 | >> | PMP-4125 POWER | L-41-224
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | FAN-4151 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | BACKWASH VALVE VAULT LIGHTING | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #6 | >> | BACKWASH VALVE VAULT RECEPTACLE | 0
L-41-226 | 02E01 | 2 | 2 | #4 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | PB-15 |  |  |  | L-41-227
|  |  | 2 | #6 | XHHW-2 |  |  | 0 | TO: | PB-14
|  |  | 4 | #12 | XHHW-2 |  |  | 0 |  | 2 | #4 | >> | PMP-4125 POWER | L-41-225
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | FAN-4151 POWER | L-41-225
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | BACKWASH VALVE VAULT LIGHTING | L-41-225
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #6 | >> | BACKWASH VALVE VAULT RECEPTACLE | L-41-225
L-41-227 | 02E01 | 2 | 2 | #4 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | PB-14
|  |  | 2 | #6 | XHHW-2 |  |  | 0 | TO: | PNL-CS
|  |  | 4 | #12 | XHHW-2 |  |  | 0 |  | 2 | #4 | >> | PMP-4125 POWER | L-41-226
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | FAN-4151 POWER | L-41-226
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | BACKWASH VALVE VAULT LIGHTING | L-41-226
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #6 | >> | BACKWASH VALVE VAULT RECEPTACLE | L-41-226
P-41-211 | 41E01 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | FV-4112 |  |  |  | P-41-212
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | DISC-4112
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4112 POWER | 0
CONDUIT SCHEDULE AREA 41 | [12 empty] | ENGINEER | SKB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
BACKWASH TANK AND VAULT | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-41-212 | 41E01 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-4112 |  |  |  | P-41-223
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | CONDUIT TEE
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4112 POWER | P-41-211
P-41-221 | 41E01 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | FV-4122 |  |  |  | P-41-222
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | DISC-4122
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4122 POWER | 0
P-41-222 | 41E01 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-4112 |  |  |  | P-41-223
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | CONDUIT TEE
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4122 POWER | P-41-221
P-41-223 | 02E01 | 2 | 6 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | CONDUIT TEE |  |  |  | P-41-224
| 41E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4112 POWER | P-41-212
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4122 POWER | P-41-222
P-41-224 | 02E01 | 2 | 6 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PB-15 |  |  |  | P-41-225
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4112 POWER | P-41-223
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4122 POWER | P-41-223
P-41-225 | 02E01 | 2 | 6 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4112 POWER | P-41-224
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | FV-4122 POWER | P-41-224
P-41-411 | 30E04 | 3.5 | 1 | 3/C-#4/0:VFD | VFD | 0 |  | INTEGRAL | FR: | PMP-4101
|  |  | 2 | #12 | XHHW-2 |  |  | 0 | TO: | VFD-4101
|  |  | 2 | #14 | XHHW-2 |  |  | 0 |  | 1 | 3/C-#4/0:VFD | >> | PMP-4101 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-4101 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-4101 CONTROL | 0
P-41-412 | 30E09 | 2.5 | 3 | 350 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | VFD-4101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-A
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | VFD-4101 POWER | 0
P-41-421 | 30E04 | 3.5 | 1 | 3/C-#4/0:VFD | VFD | 0 |  | INTEGRAL | FR: | PMP-4102
|  |  | 2 | #12 | XHHW-2 |  |  | 0 | TO: | VFD-4102
|  |  | 2 | #14 | XHHW-2 |  |  | 0 |  | 1 | 3/C-#4/0:VFD | >> | PMP-4102 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-4102 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-4102 CONTROL | 0
P-41-422 | 30E09 | 2.5 | 3 | 350 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | VFD-4102
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-A1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | VFD-4102 POWER | 0
S-41-121 | 41E01 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-4122
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-4122
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-4122 SIGNAL | 0
S-41-122 | 02E01 | 2 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | LIT-4122 |  |  |  | S-41-123
| 41E01 |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-4122 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | LIT-4122 POWER (24VDC) | 0
S-41-123 | 02E01 | 2 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | PB-14
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-4122 SIGNAL | S-41-122
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | LIT-4122 POWER (24VDC) | S-41-122
S-41-412 | 30E09 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VFD-4101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-ELEC1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | VFD-4101 SIGNAL | 0
S-41-422 | 30E09 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VFD-4102
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-ELEC1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | VFD-4102 SIGNAL | 0
X-41-311 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | BACKWASH TANK VAULT |  |  |  | X-41-312
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-41-312 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-15 |  |  |  | X-41-313
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-41-311
X-41-313 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | STUB-UP IN CAUSTIC SODA ELEC ROOM
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | X-41-312
CONDUIT SCHEDULE AREA 41 | [12 empty] | ENGINEER | SKB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
BACKWASH TANK AND VAULT | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
X-41-351 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | STUB-UP AT BACKWASH TANK
| 41E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-15
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-41-361 | 02E01 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | STUB-UP AT BACKWASH TANK
| 41E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | PB-14
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
END OF CONDUIT SCHEDULE
END OF SECTION
THIS PAGE INTENTIONALLY LEFT BLANK