## Print - Specs
SECTION 16990D
CONDUIT SCHEDULE
AREA 55
PART 1 GENERAL
1.01 SUMMARY
| A. |  | Conduit requirements:
1. As defined in Section 16050 and Section 16130.
| B. |  | Cable requirements and definitions:
1. As defined in Section 16050 and Section 16123.
|  |  | 2. PULL: |  |  |  | Pull Rope.
PART 2 PRODUCTS
Not Used.
PART 3 EXECUTION
3.01 CONDUIT SCHEDULE
| A. |  | Conduit Schedule is presented on the following pages.
CONDUIT SCHEDULE AREA 55 | [12 empty] | ENGINEER | SKB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CULINARY PUMP STATION | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-55-201 | 55E01 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | ATS-5501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | ATS-5501 CONTROL | 0
C-55-202 | 02E02 | 2 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | GEN-5501
| 55E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | GEN-5501 CONTROL | 0
C-55-211 | 02E02 | 2 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | ATS-5501
| 55E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | GEN-5501
|  |  | 0 | 0 | 0 |  |  | 0 |  | 12 | #14 | >> | ATS-5501 CONTROL | 0
L-55-202 | 02E02 | 2 | 4 | #8 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | GEN-5501
| 55E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | PANEL CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #8 | >> | GEN-5501 POWER | 0
L-55-252 | 02E02 | 2 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | SWBD-CPS
| 55E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | SWBD-CPS POWER | 0
P-55-101 | 02E02 | 4 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | GEN-5501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | GEN-5501 POWER | 0
P-55-102 | 02E02 | 4 | 3 | 350 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | GEN-5501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 350 | >> | GEN-5501 POWER | 0
P-55-111 | 02E02 | 4 | 3 | #4/0 | XHHW-2 | 1 | #3 | XHHW-2 | FR: | SWBD-CPS
| 55E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | ATS-5501
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | SWBD-CPS POWER | 0
P-55-112 | 02E02 | 4 | 3 | #4/0 | XHHW-2 | 1 | #3 | XHHW-2 | FR: | SWBD-CPS
| 55E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | ATS-5501
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | SWBD-CPS POWER | 0
P-55-121 | 55E01 | 2 | 3 | #2/0 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | ATS-5501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #2/0 | >> | ATS-5501 POWER | 0
P-55-122 | 55E01 | 2 | 3 | #2/0 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | ATS-5501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #2/0 | >> | ATS-5501 POWER | 0
P-55-301 | 55E01 | 2 | 3 | #2/0 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | MCC-CPS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | ATS-5501
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #2/0 | >> | MCC-CPS POWER | 0
P-55-302 | 55E01 | 2 | 3 | #2/0 | XHHW-2 | 1 | #1 | XHHW-2 | FR: | MCC-CPS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | ATS-5501
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #2/0 | >> | MCC-CPS POWER | 0
X-55-401 | 02E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | GEN-5501
| 55E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | STUB-UP AT CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-55-402 | 02E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | GEN-5501
| 55E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | STUB-UP AT CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-55-421 | 02E02 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | GEN-5501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-55-422 | 02E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | GEN-5501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-55-423 | 02E02 | 2 | 1 | PULL | ROPE | 0 |  | 0 | FR: | GEN-5501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SWBD-CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
X-55-425 | 02E02 | 4 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SWBD-CPS
| 55E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | STUB-UP AT CPS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
END OF CONDUIT SCHEDULE
END OF SECTION
THIS PAGE INTENTIONALLY LEFT BLANK