## Print - Specs
SECTION 16990E
CONDUIT SCHEDULE
AREA 62 & 66
PART 1 GENERAL
1.01 SUMMARY
| A. |  | Conduit requirements:
1. As defined in Section 16050 and Section 16130.
| B. |  | Cable requirements and definitions:
1. As defined in Section 16050 and Section 16123.
|  |  | 2. 2/CS#16: |  |  |  | 2 conductor, 16 gauge, twisted shielded pair.
|  |  | 3. PULL: |  |  |  | Pull Rope.
PART 2 PRODUCTS
Not Used.
PART 3 EXECUTION
3.01 CONDUIT SCHEDULE
| A. |  | Conduit Schedule is presented on the following pages.
CONDUIT SCHEDULE AREA 62 & 66 | [12 empty] | ENGINEER | SKB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
PRIMARY COAGULANT BUILDING & FLUORIDE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-62-201 | 71E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-6201
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | RTU-PEA CONTROL | 0
C-62-211 | 62E01 | 0.75 | 3 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6201 |  |  |  | C-62-225
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISH-6201 CONTROL | 0
C-62-221 | 62E01 | 0.75 | 3 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6202 |  |  |  | C-62-225
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISH-6202 CONTROL | 0
C-62-225 | 01E03 | 1 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | J-BOX
| 62E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CDS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISH-6201 CONTROL | C-62-211
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISH-6202 CONTROL | C-62-221
C-62-251 | 77E01 | 1.5 | 48 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | MCC-CDS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CDS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 24 | #14 | >> | FVNR-6201 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 24 | #14 | >> | FVNR-6202 CONTROL | 0
C-62-311 | 62E01 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6201 |  |  |  | C-62-325
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | LCP-6201 CONTROL | 0
C-62-321 | 62E01 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6202 |  |  |  | C-62-325
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | LCP-6202 CONTROL | 0
C-62-325 | 01E03 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | J-BOX
| 62E01 |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CDS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | LCP-6201 CONTROL | C-62-311
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | LCP-6202 CONTROL | C-62-321
P-62-211 | 01E03 | 1 | 5 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-6201
| 62E01 |  | 2 | #14 | XHHW-2 |  |  | 0 | TO: | MCC-CDS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PMP-6201 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-6201 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6201 CONTROL | 0
P-62-221 | 01E03 | 1 | 5 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-6202
| 62E01 |  | 2 | #14 | XHHW-2 |  |  | 0 | TO: | MCC-CDS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PMP-6202 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-6202 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6202 CONTROL | 0
X-62-411 | 01E03 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | PRIMARY COAGULANT BUILDING
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CDS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
L-66-111 | 66E01 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | FIT-6691
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | FIT-6691 POWER | 0
S-66-111 | 66E01 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FIT-6691
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-FL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | FIT-6691 SIGNAL | 0
END OF CONDUIT SCHEDULE
END OF SECTION
THIS PAGE INTENTIONALLY LEFT BLANK