## Print - Specs
SECTION 16990F
CONDUIT SCHEDULE
AREA 63
PART 1 GENERAL
1.01 SUMMARY
| A. |  | Conduit requirements:
1. As defined in Section 16050 and Section 16130.
| B. |  | Cable requirements and definitions:
1. As defined in Section 16050 and Section 16123.
|  |  | 2. 2/CS#16: |  |  |  | 2 conductor, 16 gauge, twisted shielded pair.
|  |  | 3. */FO: |  |  |  | Fiber optic (* indicates strand count).
|  |  | 4. CAT6: |  |  |  | Category 6 Ethernet cable.
|  |  | 5. PULL: |  |  |  | Pull Rope.
PART 2 PRODUCTS
Not Used.
PART 3 EXECUTION
3.01 CONDUIT SCHEDULE
| A. |  | Conduit Schedule is presented on the following pages.
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-63-001 | 63E03 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6301
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6301
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6301 CONTROL | 0
C-63-002 | 63E03 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6302
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6301
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6302 CONTROL | 0
C-63-003 | 63E03 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6303
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6303
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6303 CONTROL | 0
C-63-004 | 63E03 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6304
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6303
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6304 CONTROL | 0
C-63-005 | 63E03 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6305
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6305
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6305 CONTROL | 0
C-63-006 | 63E03 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6306
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6305
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6306 CONTROL | 0
C-63-007 | 63E03 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6307
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6307
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6307 CONTROL | 0
C-63-008 | 63E03 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6308
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6307
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6308 CONTROL | 0
C-63-009 | 63E03 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6309
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6309
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6309 CONTROL | 0
C-63-010 | 63E03 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6310
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6309
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6310 CONTROL | 0
C-63-011 | 63E04 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6311
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6311
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6311 CONTROL | 0
C-63-012 | 63E04 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6312
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6311
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6312 CONTROL | 0
C-63-013 | 63E04 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6313
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6314
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6313 CONTROL | 0
C-63-014 | 63E04 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6314
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6314
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6314 CONTROL | 0
C-63-015 | 63E04 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6315
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6316
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6315 CONTROL | 0
C-63-016 | 63E04 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6316
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6316
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6316 CONTROL | 0
C-63-017 | 63E04 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6317
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6318
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6317 CONTROL | 0
C-63-018 | 63E04 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6318
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6318
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6318 CONTROL | 0
C-63-019 | 63E04 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6319
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6320
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6319 CONTROL | 0
C-63-020 | 63E04 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FV-6320
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6320
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FV-6320 CONTROL | 0
C-63-022 | 63E03 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6301
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VCP-6301 CONTROL | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-63-024 | 63E03 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6303
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VCP-6303 CONTROL | 0
C-63-026 | 63E03 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6305
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VCP-6305 CONTROL | 0
C-63-028 | 63E03 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6307
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VCP-6307 CONTROL | 0
C-63-030 | 63E03 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6309
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VCP-6309 CONTROL | 0
C-63-032 | 63E04 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6311
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VCP-6311 CONTROL | 0
C-63-034 | 63E04 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6314
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VCP-6314 CONTROL | 0
C-63-036 | 63E04 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6316
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VCP-6316 CONTROL | 0
C-63-038 | 63E04 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6318
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VCP-6318 CONTROL | 0
C-63-040 | 63E04 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6320
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | VCP-6320 CONTROL | 0
C-63-041 | 63E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-6301
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSH-6301 CONTROL | 0
C-63-042 | 63E07 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-6302
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSH-6302 CONTROL | 0
C-63-043 | 63E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-6333
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSH-6333 CONTROL | 0
C-63-044 | 63E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-6331
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSH-6331 CONTROL | 0
C-63-051 | 63E02 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6331
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 12 | #14 | >> | VCP-6331 CONTROL | 0
C-63-052 | 63E02 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6332
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 12 | #14 | >> | VCP-6332 CONTROL | 0
C-63-053 | 63E02 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6333
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 12 | #14 | >> | VCP-6333 CONTROL | 0
C-63-054 | 63E02 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6334
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 12 | #14 | >> | VCP-6334 CONTROL | 0
C-63-055 | 63E02 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6335
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 12 | #14 | >> | VCP-6335 CONTROL | 0
C-63-056 | 63E02 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6336
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 12 | #14 | >> | VCP-6336 CONTROL | 0
C-63-060 | 63E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISL-6350
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISL-6350 CONTROL | 0
C-63-062 | 63E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISL-6352
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISL-6352 CONTROL | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-63-063 | 63E09 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSHH-6319
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSHH-6319 CONTROL | 0
C-63-071 | 63E08 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | BLR-6391
|  |  | 2 | #14 | XHHW-2 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-6391 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6391 CONTROL | 0
C-63-072 | 63E08 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | BLR-6392
|  |  | 2 | #14 | XHHW-2 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-6392 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6392 CONTROL | 0
C-63-073 | 63E08 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-6391
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-6391 CONTROL POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-6391 CONTROL | 0
C-63-074 | 63E08 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-6392
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-6392 CONTROL POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSL-6392 CONTROL | 0
C-63-075 | 63E08 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6391
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | LCP-6391 CONTROL | 0
C-63-076 | 63E08 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6392
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | LCP-6392 CONTROL | 0
C-63-081 | 63E12 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | HP-6351
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AHU-6351
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | HP-6351 CONTROL | 0
C-63-082 | 63E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | TSHL-6351
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AHU-6351
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | TSHL-6351 CONTROL | 0
C-63-083 | 63E12 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | HP-6352
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AHU-6352
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | HP-6352 CONTROL | 0
C-63-084 | 63E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | TSHL-6352
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AHU-6352
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | TSHL-6352 CONTROL | 0
C-63-085 | 63E05 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PPU-6353
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 12 | #14 | >> | PPU-6353 CONTROL | 0
C-63-086 | 63E07 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | TSHL-6354
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MAU-6354
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | TSHL-6354 CONTROL | 0
C-63-087 | 63E12 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | XS-6354
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MAU-6354
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | XS-6354 CONTROL | 0
C-63-088 | 63E12 | 1 | 14 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | MAU-6354
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 14 | #14 | >> | MAU-6354 CONTROL | 0
C-63-089 | 63E10 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LVR-6355
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LVR-6355 (24VDC) CONTROL | 0
C-63-090 | 63E12 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | XS-6355
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | XS-6355 CONTROL | 0
C-63-092 | 63E09 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LVR-6356
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LVR-6356 (24VDC) CONTROL | 0
C-63-093 | 63E12 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | XS-6356
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | XS-6356 CONTROL | 0
C-63-095 | 63E02 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FVNR-6368
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | LCP-6368 CONTROL | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-63-096 | 63E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | TSH-6368
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FVNR-6368
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6368 CONTROL | 0
C-63-097 | 63E02 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FVNR-6357
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | LCP-6357 CONTROL | 0
C-63-098 | 63E11 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LVR-6357
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LVR-6357 (24VDC) CONTROL | 0
C-63-100 | 63E05 | 1.5 | 28 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | CL-6301 SPD FAIL STATUS | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | EF-6355 STARTER CONTROLS | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | EF-6356 STARTER CONTROLS | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | RVSS-6391 CONTROLS | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | RVSS-6392 CONTROLS | 0
C-63-101 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | ZSC-6381
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | ZSC-6381 CONTROL | 0
C-63-102 | 63E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | ZSC-6382
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | ZSC-6382 CONTROL | 0
C-63-103 | 63E07 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | ZSC-6383
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | ZSC-6383 CONTROL | 0
C-63-104 | 63E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | ZSC-6384
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | ZSC-6384 CONTROL | 0
C-63-105 | 63E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | ZSC-6385
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | ZSC-6385 CONTROL | 0
C-63-106 | 63E09 | 1 | 15 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6381
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 15 | #14 | >> | LCP-6381 CONTROL | 0
C-63-107 | 63E10 | 1 | 15 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6382
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 15 | #14 | >> | LCP-6382 CONTROL | 0
C-63-108 | 63E07 | 1 | 15 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6383
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 15 | #14 | >> | LCP-6383 CONTROL | 0
C-63-109 | 63E02 | 1 | 15 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6384
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 15 | #14 | >> | LCP-6384 CONTROL | 0
C-63-110 | 63E02 | 1 | 15 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6385
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 15 | #14 | >> | LCP-6385 CONTROL | 0
C-63-111 | 63E05 | 1.5 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | RVSS-6391 FAIL (24VDC) STATUS | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | RVSS-6392 FAIL (24VDC) STATUS | 0
C-63-112 | 63E05 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | EF-6355 START CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | EF-6356 START CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | EF-6357 START CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | SF-6358 START CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | RVSS-6391 START CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | RVSS-6392 START CONTROL | 0
C-63-113 | 63E05 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PANEL-MOUNTED BEACONS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | BEACON CONTROLS | 0
C-63-114 | 63E11 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | XH3-6361 & XH5-6361
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | CL2 STORAGE HORN & STROBE CONTROLS | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-63-115 | 63E11 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | XH2-6361 & XH4-6361
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | CL2 FEED HORN & STROBE CONTROLS | 0
C-63-116 | 63E09 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | ZSC-6386
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | ZSC-6386 CONTROL | 0
C-63-117 | 63E10 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | ZSC-6387
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | ZSC-6387 CONTROL | 0
C-63-611 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | DOOR 63-D102-03 SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-63-621 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | DOOR 63-D102-02 SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-63-631 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | DOOR 63-D105-01 SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-63-641 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | DOOR 63-D104-01 SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-63-651 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | DOOR 63-D103-01 SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-63-661 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | DOOR 63-D101-01 SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-63-671 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | DOOR 63-D101-02 SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
L-63-021 | 63E03 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6301
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6301 POWER | 0
L-63-023 | 63E03 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6303
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6303 POWER | 0
L-63-025 | 63E03 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6305
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6305 POWER | 0
L-63-027 | 63E03 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6307
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6307 POWER | 0
L-63-029 | 63E03 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6309
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6309 POWER | 0
L-63-031 | 63E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6311
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6311 POWER | 0
L-63-033 | 63E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6314
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6314 POWER | 0
L-63-035 | 63E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6316
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6316 POWER | 0
L-63-037 | 63E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6318
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6318 POWER | 0
L-63-039 | 63E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6320
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6320 POWER | 0
L-63-041 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | HTU-6331
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | HTU-6331 POWER | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
L-63-042 | 63E02 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HTU-6332
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HTU-6332 POWER | 0
L-63-051 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6331
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6331 POWER | 0
L-63-052 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6332
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6332 POWER | 0
L-63-053 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6333
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6333 POWER | 0
L-63-054 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6334
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6334 POWER | 0
L-63-055 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6335
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6335 POWER | 0
L-63-056 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6336
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | VCP-6336 POWER | 0
L-63-060 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PISL-6350
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PISL-6350 POWER | 0
L-63-062 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PISL-6352
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PISL-6352 POWER | 0
L-63-063 | 63E09 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-6319
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-6319 POWER | 0
L-63-071 | 63E05 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SECURITY PANEL (UTILITY) POWER | 0
L-63-072 | 63E05 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SECURITY PANEL (UPS) POWER | 0
L-63-085 | 63E12 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HP-6351 |  |  |  | L-63-087
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | CONDUIT TEE
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HP-6351 POWER | 0
L-63-086 | 63E12 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HP-6352 |  |  |  | L-63-087
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | CONDUIT TEE
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HP-6352 POWER | 0
L-63-087 | 63E12 | 0.75 | 4 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | CONDUIT TEE
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HP-6351 POWER | L-63-085
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HP-6352 POWER | L-63-086
L-63-088 | 63E10 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | LVR-6355
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | LVR-6355 POWER | 0
L-63-089 | 63E09 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | LVR-6356
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | LVR-6356 POWER | 0
L-63-090 | 63E11 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | SF-6368
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FVNR-6368
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SF-6368 POWER | 0
L-63-091 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | FVNR-6368
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | FVNR-6368 POWER | 0
L-63-093 | 63E11 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | EF-6357
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FVNR-6357
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | EF-6357 POWER | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
L-63-094 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | FVNR-6357
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | DISC-6357 POWER | 0
L-63-096 | 63E11 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | LVR-6357
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | LVR-6357 POWER | 0
L-63-097 | 63E05 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | RTU-CL (UTILITY) POWER | 0
L-63-098 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | LOI-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | LOI-CL (UPS) POWER | 0
L-63-099 | 63E05 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | LCP-6361 (UPS) POWER | 0
L-63-100 | 63E05 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | RTU-CL (UPS) POWER | 0
L-63-101 | 63E11 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6358
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | GUH-6358 POWER | 0
L-63-102 | 63E11 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6359
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | GUH-6359 POWER | 0
L-63-103 | 63E11 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6360
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | GUH-6360 POWER | 0
L-63-104 | 63E11 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6361
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | GUH-6361 POWER | 0
L-63-105 | 63E11 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6362
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | GUH-6362 POWER | 0
L-63-106 | 63E11 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6363
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | GUH-6363 POWER | 0
L-63-107 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6364
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | GUH-6364 POWER | 0
L-63-108 | 63E05 | 1 | 3 | #6 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UPS BYPASS DISC
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #6 | >> | UPS-CL (BYPASS) POWER | 0
L-63-109 | 63E05 | 1 | 3 | #6 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | UPS BYPASS DISC
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #6 | >> | UPS BYPASS DISC POWER | 0
L-63-110 | 63E05 | 3 | 4 | 250 | XHHW-2 | 1 | #2 | XHHW-2 | FR: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | 250 | >> | PNL-CL POWER | 0
L-63-111 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | TWH-6365
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | TWH-6365 POWER | 0
L-63-112 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | TWH-6366
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | TWH-6366 POWER | 0
L-63-113 | 63E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | TWH-6367
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | TWH-6367 POWER | 0
L-63-120 | 63E05 | 1 | 3 | #6 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | PNL-UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #6 | >> | PNL-UPS-CL POWER | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
N-63-100 | 63E05 | 1 | 3 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | SSM-6301 POWER MONITOR NETWORK | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | RVSS-6391 NETWORK | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | RVSS-6392 NETWORK | 0
N-63-101 | 63E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | LCP-6361 NETWORK | 0
N-63-102 | 63E05 | 4 | 1 | 0 | 12/FO | 1 | #14 | XHHW-2 | FR: | LOI-FB
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 12/FO | >> | LOI-FB NETWORK | 0
N-63-103 | 63E05 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | LOI-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6361
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | LOI-CL NETWORK | 0
N-63-611 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SECURITY CAMERA J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-63-621 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SECURITY CAMERA J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-63-631 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SECURITY CAMERA J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-63-641 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SECURITY CAMERA J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-63-651 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SECURITY CAMERA J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-63-661 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SECURITY CAMERA J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-63-671 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SECURITY CAMERA J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-63-681 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | WIRELESS NETWORK J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-63-682 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | WIRELESS NETWORK J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-63-683 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | WIRELESS NETWORK J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-63-684 | 63E16 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | WIRELESS NETWORK J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
P-63-001 | 63E08 | 1 | 3 | #6 | XHHW-2 | 1 | #8 | XHHW-2 | FR: | BLR-6391
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #6 | >> | BLR-6391 POWER | 0
P-63-002 | 63E08 | 1 | 3 | #6 | XHHW-2 | 1 | #8 | XHHW-2 | FR: | BLR-6392
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #6 | >> | BLR-6392 POWER | 0
P-63-003 | 63E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PPU-6353
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | DISC-6353
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PPU-6353 POWER | 0
P-63-004 | 63E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-6353
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-6353 POWER | 0
P-63-005 | 63E12 | 0.75 | 3 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | MAU-6354
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #10 | >> | MAU-6354 POWER | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-63-006 | 63E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | EF-6355
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | EF-6355 POWER | 0
P-63-007 | 63E12 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | EF-6356
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | EF-6356 POWER | 0
P-63-008 | 63E05 | 0.75 | 3 | #8 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | UPS-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #8 | >> | UPS (MAIN) POWER | 0
P-63-009 | 63E05 | 2.5 | 3 | 250 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | PP-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 250 | >> | PP-CL POWER | 0
P-63-010 | 63E05 | 2 | 3 | #4/0 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | XFMR-CL
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | XFMR-CL POWER | 0
P-63-011 | 63E09 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | CHLORINE BRIDGE CRANE
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | BRIDGE CRANE DISCONNECT
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | CHLORINE BRIDGE CRANE POWER | 0
P-63-012 | 63E09 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | BRIDGE CRANE DISCONNECT
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | BRIDGE CRANE DISCONNECT POWER | 0
P-63-013 | 63E09 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | OHD-6311
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | DISC-6311
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | OHD-6311 POWER | 0
P-63-014 | 63E09 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-6311
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-6311 POWER | 0
P-63-015 | 63E10 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | OHD-6312
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | DISC-6312
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | OHD-6312 POWER | 0
P-63-016 | 63E10 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-6312
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | DISC-6312 POWER | 0
S-63-001 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6301
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6301 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6301 (24VDC) POWER | 0
S-63-002 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6302
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6302 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6302 (24VDC) POWER | 0
S-63-003 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6303
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6303 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6303 (24VDC) POWER | 0
S-63-004 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6304
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6304 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6304 (24VDC) POWER | 0
S-63-005 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6305
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6305 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6305 (24VDC) POWER | 0
S-63-006 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6306
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6306 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6306 (24VDC) POWER | 0
S-63-007 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6307
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6307 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6307 (24VDC) POWER | 0
S-63-008 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6308
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6308 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6308 (24VDC) POWER | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-63-009 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6309
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6309 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6309 (24VDC) POWER | 0
S-63-010 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6310
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6310 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6310 (24VDC) POWER | 0
S-63-011 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6311
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6311 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6311 (24VDC) POWER | 0
S-63-012 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6312
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6312 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6312 (24VDC) POWER | 0
S-63-013 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6313
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6313 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6313 (24VDC) POWER | 0
S-63-014 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6314
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6314 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6314 (24VDC) POWER | 0
S-63-015 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6315
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6315 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6315 (24VDC) POWER | 0
S-63-016 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6316
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6316 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6316 (24VDC) POWER | 0
S-63-017 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6317
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6317 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6317 (24VDC) POWER | 0
S-63-018 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6318
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6318 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6318 (24VDC) POWER | 0
S-63-019 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6319
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6319 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6319 (24VDC) POWER | 0
S-63-020 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6320
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6320 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6320 (24VDC) POWER | 0
S-63-021 | 63E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6311
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6311 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6311 (24VDC) POWER | 0
S-63-022 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6312
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6312 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6312 (24VDC) POWER | 0
S-63-023 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6313
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6313 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6313 (24VDC) POWER | 0
S-63-024 | 63E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6314
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6314 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6314 (24VDC) POWER | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-63-025 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6315
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6315 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6315 (24VDC) POWER | 0
S-63-026 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6316
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6316 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6316 (24VDC) POWER | 0
S-63-027 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6317
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6317 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6317 (24VDC) POWER | 0
S-63-028 | 63E07 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6318
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6318 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6318 (24VDC) POWER | 0
S-63-031 | 63E09 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6321
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6321 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6321 (24VDC) POWER | 0
S-63-032 | 63E10 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6322
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6322 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6322 (24VDC) POWER | 0
S-63-033 | 63E09 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6323
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6323 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6323 (24VDC) POWER | 0
S-63-034 | 63E10 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6324
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6324 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6324 (24VDC) POWER | 0
S-63-035 | 63E08 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6391
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6391 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6391 (24VDC) POWER | 0
S-63-036 | 63E08 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6392
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6392 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6392 (24VDC) POWER | 0
S-63-037 | 63E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6331
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6331 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6331 (24VDC) POWER | 0
S-63-038 | 63E08 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PDIT-6391
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PDIT-6391 SIGNAL | 0
S-63-039 | 63E08 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PDIT-6392
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | PDIT-6392 SIGNAL | 0
S-63-042 | 63E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | AIT-6342
|  |  | 1 | 2/CS-#16 | 0 |  |  | 0 | TO: | LCP-6361 (RTU-CLIP)
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | AIT-6342 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | AIT-6342 (24VDC) POWER | 0
S-63-051 | 63E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-6331
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | VCP-6331 SIGNAL | 0
S-63-052 | 63E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-6332
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | VCP-6332 SIGNAL | 0
S-63-053 | 63E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-6333
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | VCP-6333 SIGNAL | 0
S-63-054 | 63E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-6334
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | VCP-6334 SIGNAL | 0
CONDUIT SCHEDULE AREA 63 | [12 empty] | ENGINEER | MJG
JVWTP FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CHLORINE BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-63-055 | 63E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-6335
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | VCP-6335 SIGNAL | 0
S-63-056 | 63E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-6336
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | VCP-6336 SIGNAL | 0
S-63-058 | 63E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TE-6359
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | TIT-6359
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TE-6359 SIGNAL | 0
S-63-059 | 63E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TIT-6359
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TIT-6359 SIGNAL | 0
S-63-060 | 63E07 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TE-6357
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | TIT-6357
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TE-6357 SIGNAL | 0
S-63-061 | 63E07 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TIT-6357
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TIT-6357 SIGNAL | 0
S-63-062 | 63E10 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TE-6358
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | TIT-6358
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TE-6358 SIGNAL | 0
S-63-063 | 63E10 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TIT-6358
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TIT-6358 SIGNAL | 0
S-63-064 | 63E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TE-6360
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | TIT-6360
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TE-6360 SIGNAL | 0
S-63-065 | 63E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TIT-6360
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TIT-6360 SIGNAL | 0
END OF CONDUIT SCHEDULE
END OF SECTION