## Print - Specs
SECTION 16990G
CONDUIT SCHEDULE
AREA 65
PART 1 GENERAL
1.01 SUMMARY
| A. |  | Conduit requirements:
1. As defined in Section 16050 and Section 16130.
| B. |  | Cable requirements and definitions:
1. As defined in Section 16050 and Section 16123.
|  |  | 2. 2/CS#16: |  |  |  | 2 conductor, 16 gauge, twisted shielded pair.
|  |  | 3. */C#Y: |  |  |  | Multiconductor cable (* indicates number of
conductors, Y indicates conductor size and insulation).
|  |  | 4. CAT6: |  |  |  | Category 6 Ethernet cable.
|  |  | 5. MFR: |  |  |  | Manufacturer or vendor furnished cable.
|  |  | 6. PULL: |  |  |  | Pull Rope.
|  |  | 7. VFD: |  |  |  | Shielded VFD cable with integral ground.
PART 2 PRODUCTS
Not Used.
PART 3 EXECUTION
3.01 CONDUIT SCHEDULE
| A. |  | Conduit Schedule is presented on the following pages.
CONDUIT SCHEDULE AREA 65 | [12 empty] | ENGINEER | CK
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CAUSTIC SODA BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-65-001 | 65E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-6517
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSH-6517 CONTROL | 0
C-65-005 | 65E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-6516
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSH-6516 HIGH FLOW CONTROL | 0
C-65-007 | 65E03 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | TSHL-6560
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6560
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSHL-6560 CONTROL | 0
C-65-008 | 65E03 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSL-6560
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | FSL-6560 LOW FLOW CONTROL | 0
C-65-009 | 65E02 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | XS-6560
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6560
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | XS-6560 CONTROL | 0
C-65-010 | 65E06 | 1 | 14 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | MAU-6560
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 14 | #14 | >> | MAU-6560 CONTROL | 0
C-65-015 | 65E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | TSHL-6551
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AHU-6551
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSHL-6551 CONTROL | 0
C-65-016 | 65E02 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AHU-6551
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | CU-6551
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AHU-6551 CONTROL | 0
C-65-017 | 65E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | TSHL-6552
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | AHU-6552
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSHL-6552 CONTROL | 0
C-65-018 | 65E02 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | AHU-6552
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | CU-6552
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | AHU-6552 CONTROL | 0
C-65-019 | 65E02 | 1 | 12 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PPU-6553
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PPU-6553 SMOKE SHUT DOWN | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PPU-6553 FAILED | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PPU-6553 RUNNING | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PPU-6553 DIRTY FILTER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PPU-6553 LOW TEMP | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PPU-6553 START | 0
C-65-021 | 65E04 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6572
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | PISH-6572 HIGH PRESSURE CONTROL | 0
C-65-022 | 65E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | SV-6584
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | SV-6584 OPEN CONTROL | 0
C-65-023 | 65E02 | 2 | 78 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | MCC-CS SPD FAIL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FVNR-6554 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FVNR-6555 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | FVNR-6556 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 14 | #14 | >> | VFD-6572 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 14 | #14 | >> | VFD-6582 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FVNR-6511 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | FVNR-6521 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | SSM-6501 | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | SPD-6501 | 0
C-65-024 | 65E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6541
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-6541 HIGH PRESSURE CONTROL | 0
C-65-025 | 65E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6562
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-6562 HIGH PRESSURE CONTROL | 0
C-65-026 | 65E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6511
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-6511 HIGH PRESSURE CONTROL | 0
C-65-027 | 65E05 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6521
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | PISH-6521 HIGH PRESSURE CONTROL | 0
CONDUIT SCHEDULE AREA 65 | [12 empty] | ENGINEER | CK
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CAUSTIC SODA BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-65-029 | 65E03 | 1 | 14 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6560
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 14 | #14 | >> | LCP-6560 CONTROL | 0
C-65-031 | 65E06 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LCP-6555
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LCP-6555 AUTO CONTROL | 0
C-65-032 | 65E04 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | XS-6556
| 65E06 |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | XS-6556 SMOKE DETECTOR CONTROL | 0
C-65-035 | 65E04 | 1 | 14 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PMP-6541
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 14 | #14 | >> | PMP-6541 CONTROL | 0
C-65-036 | 65E04 | 1 | 14 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PMP-6562
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 14 | #14 | >> | PMP-6562 CONTROL | 0
C-65-039 | 65E06 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6554
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-6554 FVNR-6554 CONTROL | 0
C-65-040 | 65E06 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6555
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-6555 FVNR-6555 CONTROL | 0
C-65-042 | 65E06 | 0.75 | 7 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6556
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 7 | #14 | >> | LCP-6556 FVNR-6556 CONTROL | 0
C-65-044 | 65E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6582
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-6582 VFD-6582 CONTROL | 0
C-65-045 | 65E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6582
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-6582N HIGH PRESS CONTROL | 0
C-65-047 | 65E05 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6521
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-6521 FVNR-6521 CONTROL | 0
C-65-049 | 65E05 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | TIT-6557
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | TE-6557
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | TIT-6557 CONTROL | 0
C-65-050 | 65E03 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | TIT-6568
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | TE-6568
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | TIT-6568 CONTROL | 0
C-65-051 | 65E02 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | TIT-6559
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | TE-6559
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | TIT-6559 MFR CONTROL | 0
C-65-510 | 65E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-6510
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSH-6510 CONTROL | 0
C-65-534 | 65E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6534
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-6534 CONTROL | 0
C-65-554 | 65E05 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | XS-6554
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS VIA FVNR-6554
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | XS-6554 CONTROL | 0
C-65-555 | 65E05 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | XS-6555
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS VIA FVNR-6555
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #14 | >> | XS-6555 CONTROL | 0
C-65-584 | 65E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-6584
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSH-6584 CONTROL | 0
C-65-611 | 65E10 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | DOOR 65-D101-01 SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-65-621 | 65E10 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | DOOR 65-D103-01 SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
CONDUIT SCHEDULE AREA 65 | [12 empty] | ENGINEER | CK
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CAUSTIC SODA BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-65-631 | 65E10 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | DOOR 65-D102-01 SECURITY J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
C-65-650 | 65E04 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-6500
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | LCP-6500 CONTROL | 0
L-65-007 | 65E02 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-UPS-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | RTU-CS POWER | 0
L-65-010 | 65E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PISH-6582
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PISH-6582 POWER | 0
L-65-011 | 65E02 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | RTU-CS POWER | 0
L-65-012 | 65E02 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | RTU-CS POWER | 0
L-65-015 | 65E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | WIT-6531
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | WIT-3631 POWER | 0
L-65-016 | 65E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PISH-6541
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PISH-6541 POWER | 0
L-65-017 | 65E04 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-6562
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-6562 HIGH PRESSURE CONTROL | 0
L-65-019 | 65E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-6541
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-6541 POWER | 0
L-65-020 | 65E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-6562
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-6562 POWER | 0
L-65-021 | 65E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | FIT-6583
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | FIT-6583 POWER | 0
L-65-022 | 65E05 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | LSH-6514
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | LSH-6514 POWER | 0
L-65-023 | 65E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | FIT-6563
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | FIT-6563 POWER | 0
L-65-501 | 65E05 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HTU-6501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HTU-6501 POWER | 0
L-65-502 | 65E05 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HTU-6502
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HTU-6502 POWER | 0
L-65-503 | 65E05 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HTU-6503
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HTU-6503 POWER | 0
L-65-030 | 65E02 | 1 | 3 | #6 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | PNL-UPS-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UPS-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #6 | >> | PNL-UPS-CS POWER | 0
L-65-031 | 65E02 | 1 | 3 | #6 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | UPS-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UPS BYPASS DISC
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #6 | >> | UPS-CS (BYPASS) POWER | 0
L-65-032 | 65E02 | 1 | 3 | #6 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | UPS BYPASS DISC
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #6 | >> | UPS BYPASS DISC POWER | 0
L-65-501 | 65E05 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HTU-6501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HTU-6501 CONTROLLER POWER | 0
CONDUIT SCHEDULE AREA 65 | [12 empty] | ENGINEER | CK
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CAUSTIC SODA BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
L-65-502 | 65E05 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HTU-6502
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HTU-6502 CONTROLLER POWER | 0
L-65-503 | 65E05 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HTU-6503
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HTU-6503 CONTROLLER POWER | 0
L-65-510 | 65E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | HTU-6510
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | HTU-6510 POWER | 0
L-65-511 | 65E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | HTU-6511
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | HTU-6511 POWER | 0
L-65-531 | 65E04 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HTU-6531
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HTU-6531 CONTROLLER POWER | 0
L-65-534 | 65E04 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | LSH-6534
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 |  | LSH-6534 POWER | 0
L-65-561 | 65E03 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6561
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | GUH-561 POWER | 0
L-65-562 | 65E04 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6562
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | GUH-6562 POWER | 0
L-65-563 | 65E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6563
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | GUH-563 POWER | 0
L-65-564 | 65E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | GUH-6564
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | GUH-564 POWER | 0
L-65-650 | 65E04 | 0.75 | 3 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | LCP-6500
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #10 | >> | LCP-6500 POWER | 0
N-65-001 | 65E02 | 0.75 | 1 | 0 | CAT6 | 1 | #14 | XHHW-2 | FR: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | CAT6 | >> | MCC-CS POWER MONITOR NETWORK | 0
N-65-611 | 65E10 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SECURITY CAMERA J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-65-621 | 65E10 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | SECURITY CAMERA J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | SECURITY PANEL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-65-631 | 65E10 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | WIRELESS NETWORK J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-65-641 | 65E10 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | WIRELESS NETWORK J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
N-65-651 | 65E10 | 1 | 1 | PULL | ROPE | 0 |  | 0 | FR: | WIRELESS NETWORK J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | PULL | >> | SPARE | 0
P-65-001 | 65E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-6554
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | EF-6554
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | EF-6554 POWER | P-65-002
P-65-002 | 65E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-6554 |  |  |  | P-65-001
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | EF-6554 POWER | 0
P-65-004 | 65E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | EF-6555 |  |  |  | P-65-024
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | DISC-6555
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | EF-6555 POWER | 0
P-65-005 | 65E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | SF-6556 |  |  |  | P-65-006
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | DISC-6556
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | SF-6556 POWER | 0
CONDUIT SCHEDULE AREA 65 | [12 empty] | ENGINEER | CK
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CAUSTIC SODA BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-65-006 | 65E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-6556
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | SF-6556 POWER | P-65-005
P-65-007 | 65E02 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PPU-6553 |  |  |  | P-65-008
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | DISC-6553
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PPU-6553 POWER | 0
P-65-008 | 65E02 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-6553
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PPU-6553 POWER | P-65-007
P-65-013 | 65E03 | 0.75 | 3 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | LCP-6560
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #10 | >> | LCP-6560 POWER | 0
P-65-016 | 65E04 | 1.5 | 1 | 3/C-#12:VFD | VFD | 0 |  | INTEGRAL | FR: | PMP-6572
|  |  | 4 | #14 | XHHW-2 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 3/C-#12:VFD | >> | PMP-6572 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PMP-6572 MWH CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PMP-6572 TSH CONTROL | 0
P-65-018 | 65E04 | 1.5 | 1 | 3/C-#12:VFD | VFD | 0 |  | INTEGRAL | FR: | PMP-6582
|  |  | 4 | #14 | XHHW-2 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 3/C-#12:VFD | >> | PMP-6582 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PMP-6582 MWH CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PMP-6582 TSH CONTROL | 0
P-65-020 | 65E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-6511
|  |  | 4 | #14 | XHHW-2 |  |  | 0 | TO: | LCP-6511
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PMP-6511 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PMP-6511 MWH CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PMP-6511 TSH CONTROL | 0
P-65-021 | 65E05 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-6521
|  |  | 4 | #14 | XHHW-2 |  |  | 0 | TO: | LCP-6521
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PMP-6521 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PMP-6521 MWH CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PMP-6521 TSH CONTROL | 0
P-65-024 | 65E06 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | DISC-6555
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | EF-6555 POWER | P-65-004
P-65-025 | 65E06 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HP-6551 |  |  |  | P-65-026
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | DISC-6551
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HP-6551 POWER | 0
P-65-026 | 65E06 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | DISC-6551
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HP-6551 POWER | P-65-025
P-65-027 | 65E06 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | HP-6552 |  |  |  | P-65-028
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | DISC-6552
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HP-6552 POWER | 0
P-65-028 | 65E06 | 0.75 | 2 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | DISC-6552
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | HP-6552 POWER | P-65-027
P-65-030 | 65E02 | 2 | 3 | #4/0 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | XFMR-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | XFMR-CS POWER | 0
P-65-031 | 65E02 | 3 | 4 | 250 | XHHW-2 | 1 | #2 | XHHW-2 | FR: | PNL-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | 250 | >> | PNL-CS POWER | 0
P-65-040 | 65E02 | 0.75 | 3 | #8 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | UPS-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #8 | >> | UPS-CS (MAIN) POWER | 0
P-65-045 | 65E02 | 1.5 | 3 | #2 | XHHW-2 | 1 | #8 | XHHW-2 | FR: | PP-CS
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #2 | >> | PP-CS POWER | 0
P-65-600 | 65E06 | 0.75 | 3 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | MAU-6560
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #10 | >> | MAU-6560 POWER | 0
S-65-001 | 65E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LSH-6514
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LSH-6514 SIGNAL | 0
CONDUIT SCHEDULE AREA 65 | [12 empty] | ENGINEER | CK
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
CAUSTIC SODA BUILDING | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-65-002 | 65E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-6501
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-6501 SIGNAL | 0
S-65-003 | 65E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-6502
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-6502 SIGNAL | 0
S-65-004 | 65E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-6503
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-6503 SIGNAL | 0
S-65-005 | 65E04 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-6531
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-6531 SIGNAL | 0
S-65-006 | 65E04 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | WIT-3631
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-3631 SIGNAL | 0
S-65-007 | 65E05 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TIT-6557
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TIT-6557 SIGNAL | 0
S-65-008 | 65E03 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TIT-6568
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CL
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TIT-6568 SIGNAL | 0
S-65-009 | 65E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | TIT-6559
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | TIT-6559 SIGNAL | 0
S-65-010 | 65E04 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FIT-6563
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | FIT-6563 SIGNAL | 0
S-65-011 | 65E04 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | FIT-6583
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | FIT-6583 FLOW SIGNAL | 0
S-65-020 | 65E04 | 1 | 4 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PMP-6541
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | 2/CS-#16 | >> | PMP-6541 SIGNAL | 0
S-65-025 | 65E04 | 1 | 4 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PMP-6562
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | 2/CS-#16 | >> | PMP-6562 SIGNAL | 0
S-65-048 | 65E04 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | WE-6531
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | WIT-6531
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | WIT-6531 CONTROL | 0
S-65-650 | 65E04 | 1 | 3 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LCP-6500
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-CS
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | 2/CS-#16 | >> | LCP-6500 SIGNAL | 0
END OF CONDUIT SCHEDULE
END OF SECTION