## Print - Specs
SECTION 16990H
CONDUIT SCHEDULE
AREA 68
PART 1 GENERAL
1.01 SUMMARY
| A. |  | Conduit requirements:
1. As defined in Section 16050 and Section 16130.
| B. |  | Cable requirements and definitions:
1. As defined in Section 16050 and Section 16123.
|  |  | 2. 2/CS#16: |  |  |  | 2 conductor, 16 gauge, twisted shielded pair.
|  |  | 3. */C#Y: |  |  |  | Multiconductor cable (* indicates number of
conductors, Y indicates conductor size and insulation).
|  |  | 4. VFD: |  |  |  | Shielded VFD cable with integral ground.
PART 2 PRODUCTS
Not Used.
PART 3 EXECUTION
3.01 CONDUIT SCHEDULE
| A. |  | Conduit Schedule is presented on the following pages.
CONDUIT SCHEDULE AREA 68 | [12 empty] | ENGINEER | SKB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
PAC AREA | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-68-125 | 68E02 | 1.5 | 44 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PAC SILO 1 CONTROL J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6800
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-6801 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PDAH-6802 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-6801 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSL-6801 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-6803 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSHL-6803 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6802 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6804 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6825 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6811 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6812 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-6810 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6814 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 12 | #14 | >> | SPARE | 0
C-68-128 | 68E02 | 2 | 20 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PAC SILO 1 CONTROL J-BOX
|  |  | 40 | #14 | XHHW-2 |  |  | 0 | TO: | VCP-6800
|  |  | 0 | 0 | 0 |  |  | 0 |  | 16 | #14 | >> | VCP-6801 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV1-6801 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV2-6801 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV3-6801 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV4-6801 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV-6802 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV1-6804 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV2-6804 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV-6811 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV-6813A CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV-6813B CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 24 | #14 | >> | SPARE | 0
C-68-325 | 68E02 | 1.5 | 44 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PAC SILO 2 CONTROL J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6830
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LIT-6831 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PDAH-6832 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-6831 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSL-6831 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-6833 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSHL-6833 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6832 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6834 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6845 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6841 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6842 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-6840 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #14 | >> | PISL-6844 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 12 | #14 | >> | SPARE | 0
C-68-328 | 68E02 | 2 | 20 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PAC SILO 2 CONTROL J-BOX
|  |  | 40 | #14 | XHHW-2 |  |  | 0 | TO: | VCP-6830
|  |  | 0 | 0 | 0 |  |  | 0 |  | 16 | #14 | >> | VCP-6831 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV1-6831 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV2-6831 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV3-6831 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV4-6831 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV-6832 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV1-6834 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV2-6834 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV-6841 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV-6843A CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | SV-6843B CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 24 | #14 | >> | SPARE | 0
L-68-125 | 68E02 | 1 | 8 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | PAC SILO 1 120V J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PPSC-PAC
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | SILO 1 RECEPTACLES | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | SILO 1 LIGHTS | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #10 | >> | SPARE | 0
L-68-325 | 68E02 | 1 | 8 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | PAC SILO 2 120V J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PPSC-PAC
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | SILO 2 RECEPTACLES | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #10 | >> | SILO 2 LIGHTS | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 4 | #10 | >> | SPARE | 0
P-68-124 | 68E02 | 1.5 | 1 | 3/C-#12:VFD | VFD | 0 |  | INTEGRAL | FR: | PAC SILO 1 480V J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP2-6802
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 3/C-#12:VFD | >> | FDR-6803 POWER | 0
CONDUIT SCHEDULE AREA 68 | [12 empty] | ENGINEER | SKB
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
PAC AREA | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
P-68-125 | 68E02 | 1.5 | 6 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | PAC SILO 1 480V J-BOX
|  |  | 6 | #12 | XHHW-2 |  |  | 0 | TO: | VCP2-6802
|  |  | 6 | #14 | XHHW-2 |  |  | 0 |  | 2 | #12 | >> | MWH-6803 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6803 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #10 | >> | FDR-6810 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-6810 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6810 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #10 | >> | BLO-6802 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-6802 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6802 CONTROL | 0
P-68-128 | 68E02 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PAC SILO 1 480V J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-PAC
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PAC SILO 1 HEATER | 0
P-68-324 | 68E02 | 1.5 | 1 | 3/C-#12:VFD | VFD | 0 |  | INTEGRAL | FR: | PAC SILO 2 480V J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP2-6832
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 3/C-#12:VFD | >> | FDR-6833 POWER | 0
P-68-325 | 68E02 | 1.5 | 6 | #10 | XHHW-2 | 1 | #10 | XHHW-2 | FR: | PAC SILO 2 480V J-BOX
|  |  | 6 | #12 | XHHW-2 |  |  | 0 | TO: | VCP2-6832
|  |  | 6 | #14 | XHHW-2 |  |  | 0 |  | 2 | #12 | >> | MWH-6833 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6833 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #10 | >> | FDR-6840 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-6840 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6840 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #10 | >> | BLO-6832 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | MWH-6832 POWER | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | TSH-6832 CONTROL | 0
P-68-328 | 68E02 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PAC SILO 2 480V J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PP-PAC
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PAC SILO 2 HEATER | 0
S-68-125 | 68E02 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PAC SILO 1 SIGNAL J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6800
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | VCP-6801 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-6801 SIGNAL | 0
S-68-325 | 68E02 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | PAC SILO 2 SIGNAL J-BOX
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | VCP-6830
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | VCP-6831 SIGNAL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-6831 SIGNAL | 0
END OF CONDUIT SCHEDULE
END OF SECTION