## Print - Specs
SECTION 16990K
CONDUIT SCHEDULE
AREA 71
PART 1 GENERAL
1.01 SUMMARY
| A. |  | Conduit requirements:
1. As defined in Section 16050 and Section 16130.
| B. |  | Cable requirements and definitions:
1. As defined in Section 16050 and Section 16123.
|  |  | 2. 2/CS#16: |  |  |  | 2 conductor, 16 gauge, twisted shielded pair.
|  |  | 3. MFR: |  |  |  | Manufacturer or vendor furnished cable.
|  |  | 4. RS-485 |  |  |  | RS-485 cable.
PART 2 PRODUCTS
Not Used.
PART 3 EXECUTION
3.01 CONDUIT SCHEDULE
| A. |  | Conduit Schedule is presented on the following pages.
CONDUIT SCHEDULE AREA 71 | [12 empty] | ENGINEER | CK
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
PEC AREA | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-71-001 | 71E01 | 0.75 | 6 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LCP-7100
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 6 | #14 | >> | LCP-7100 CONTROL | 0
C-71-002 | 71E02 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-7107
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | PMP-7107 CONTROL | 0
C-71-003 | 71E02 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-7106
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | PMP-7106 CONTROL | 0
C-71-004 | 71E01 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PMP-7103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | PMP-7103 CONTROL | 0
C-71-005 | 71E01 | 0.75 | 8 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PMP-7104
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 8 | #14 | >> | PMP-7104 CONTROL | 0
C-71-006 | 71E02 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-7104
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-7104 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-710424 VDC POWER | 0
C-71-007 | 71E02 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | LE-7105
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | LIT-7105
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | LE-7105 CONTROL | 0
C-71-008 | 71E02 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | WE-7105
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | WIT-7105
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | WE-7105 CONTROL | 0
C-71-009 | 71E01 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FSH-7116
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FSH-7116 CONTROL | 0
C-71-010 | 71E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | MCC-PEA
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | MCC-PEA CONTROL | 0
C-71-011 | 71E02 | 0.75 | 1 | MFR | CABLE | 1 | #14 | XHHW-2 | FR: | WE-6211
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | WIT-6211
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | MFR | >> | WE-6211 CONTROL | 0
C-71-103 | 71E01 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-7103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-7103 CONTROL | 0
C-71-104 | 71E01 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-7104
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-7104 CONTROL | 0
C-71-106 | 71E02 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-7106
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-7106 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-7106 24VDC POWER | 0
C-71-107 | 71E02 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-7107
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-7107 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-7107 24VDC POWER | 0
C-71-108 | 71E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-7108
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-7108 24VDC CONTROL | 0
C-71-111 | 71E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | WIT-6211
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | WIT-6211 24VDC POWER | 0
C-71-113 | 71E01 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-7103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FVNR-7103
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-7103 CONTROL | 0
C-71-114 | 71E01 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | PISH-7104
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FVNR-7104
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | PISH-7104 CONTROL | 0
C-71-203 | 71E01 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LE-7103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LE-7103 CONTROL | 0
CONDUIT SCHEDULE AREA 71 | [12 empty] | ENGINEER | CK
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
PEC AREA | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
C-71-204 | 71E02 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6204
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | PMP-6204 CONTROL | 0
C-71-205 | 71E02 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6205
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | PMP-6205 CONTROL | 0
C-71-211 | 71E02 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6211
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | PMP-6211 CONTROL | 0
C-71-214 | 71E02 | 0.75 | 4 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | LSH-6214
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-6214 CONTROL | 0
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | LSH-6214 24VDC POWER | 0
214
C-71-215 | 71E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-6215
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-6215 24VDC POWER | 0
C-71-216 | 71E02 | 0.75 | 2 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | FIT-6216
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #14 | >> | FIT-6216 24VDC POWER | 0
C-71-221 | 71E02 | 0.75 | 10 | #14 | XHHW-2 | 1 | #14 | XHHW-2 | FR: | VCP-6221
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 10 | #14 | >> | PMP-6221 CONTROL | 0
L-71-001 | 71E01 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | LCP-7100
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | LCP-7100 POWER | 0
L-71-002 | 71E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-7107
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-7107 POWER | 0
L-71-003 | 71E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-7106
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-7106 POWER | 0
L-71-004 | 71E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | UPS-S
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | 12 | RTU-PEA POWER | 0
L-71-005 | 71E02 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | RTU-PEA POWER | 0
L-71-103 | 71E01 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PISH-7103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FVNR-7103
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PISH-7103 POWER | 0
L-71-104 | 71E01 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PISH-7104
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | FVNR-7104
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PISH-7104 POWER | 0
L-71-203 | 71E01 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | LE-7103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | LE-7103 POWER | 0
L-71-204 | 71E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6204
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-6204 POWER | 0
L-71-205 | 71E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6205
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-6205 POWER | 0
L-71-211 | 71E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6211
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-6211 POWER | 0
L-71-221 | 71E02 | 0.75 | 2 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | VCP-6221
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | PNL-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | #12 | >> | PMP-6221 POWER | 0
N-71-001 | 71E02 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | MCC-PEA
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | MCC-PEA NETWORK | 0
CONDUIT SCHEDULE AREA 71 | [12 empty] | ENGINEER | CK
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
PEC AREA | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
N-71-108 | 71E02 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-7108
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-7108 NETWORK | 0
N-71-215 | 71E02 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-6215
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-6215 NETWORK | 0
N-71-216 | 71E02 | 0.75 | 1 | 0 | RS-485 | 1 | #14 | XHHW-2 | FR: | FIT-6216
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | RS-485 | >> | FIT-6216 NETWORK | 0
P-71-001 | 71E01 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-7103
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-PEA VIA FVNR-7103
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PMP-7103 POWER | 0
P-71-002 | 71E01 | 0.75 | 3 | #12 | XHHW-2 | 1 | #12 | XHHW-2 | FR: | PMP-7104
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-PEA VIA FVNR-7104
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #12 | >> | PMP-7104 POWER | 0
P-71-003 | 71E02 | 1.5 | 3 | #2 | XHHW-2 | 1 | #8 | XHHW-2 | FR: | PP-PEA
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #2 | >> | PP-PEA POWER | 0
P-71-004 | 71E02 | 1.5 | 3 | #1/0 | XHHW-2 | 1 | #6 | XHHW-2 | FR: | PNL-PEA
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | XFMR-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #1/0 | >> | PNL-PEA POWER | 0
P-71-006 | 71E02 | 1.5 | 3 | #1/0 | XHHW-2 | 1 | #6 | XHHW-2 | FR: | XFMR-PEA
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #1/0 | >> | XFMR-PEA POWER | 0
P-71-007 | 71E02 | 2 | 3 | #4/0 | XHHW-2 | 1 | #4 | XHHW-2 | FR: | MCC-PEA
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | MCC-B1
|  |  | 0 | 0 | 0 |  |  | 0 |  | 3 | #4/0 | >> | MCC-PEA POWER | 0
S-71-001 | 71E01 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-7101
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-7101 SIGNAL | 0
S-71-002 | 71E01 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-7102
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-7102 SIGNAL | 0
S-71-003 | 71E01 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LCP-7100
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | LCP-7100 SIGNAL | 0
S-71-004 | 71E02 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-7107
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | PMP-7107 SIGNAL | 0
S-71-005 | 71E02 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-7106
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | PMP-7106 SIGNAL | 0
S-71-006 | 71E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-7105
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-7105 SIGNAL | 0
S-71-007 | 71E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | WIT-7105
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-7105 SIGNAL | 0
S-71-011 | 71E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | LIT-6211
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | LIT-6211 SIGNAL | 0
S-71-111 | 71E02 | 0.75 | 1 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | WIT-6211
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 1 | 2/CS-#16 | >> | WIT-6211 SIGNAL | 0
S-71-204 | 71E02 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-6204
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | PMP-6204 SIGNAL | 0
S-71-205 | 71E02 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-6205
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | PMP-6205 SIGNAL | 0
S-71-211 | 71E02 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-6211
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | PMP-6211 SIGNAL | 0
CONDUIT SCHEDULE AREA 71 | [12 empty] | ENGINEER | CK
FILTER AND CHEMICAL FEED UPGRADES | [12 empty] | REVISION | 0
PEC AREA | [12 empty] | DATE | 2025-04-09
CONDUIT |  |  | CONDUCTORS |  |  | GROUND
NUMBER | DWG | SIZE | # | SIZE | TYPE | # | SIZE | TYPE | DESCRIPTION |  |  |  |  | CONNECTING SEGMENTS
S-71-221 | 71E02 | 0.75 | 2 | 2/CS-#16 | 0 | 1 | #14 | XHHW-2 | FR: | VCP-6221
|  |  | 0 | 0 | 0 |  |  | 0 | TO: | RTU-PEA
|  |  | 0 | 0 | 0 |  |  | 0 |  | 2 | 2/CS-#16 | >> | PMP-6221 SIGNAL | 0
END OF CONDUIT SCHEDULE
END OF SECTION